January 31, 2024

Exterior Asbestos
	
and Lead Paint Survey Report for Repainting

www.forensicanalytical.com

Cole Elementary School 615 West Stuart Avenue Clovis, CA 93612

Prepared for:

Adam Belmont, Maintenance Dept. Manager Clovis Unified School District
1470 Herndon Avenue Clovis, CA 93611
559-327-9491 | adambelmont@cusd.com

Prepared By:

Sean Baker
Forensic Analytical Consulting Services 2440 West Shaw Avenue, Suite 105 Fresno, CA 93711
559-436-0277 | sean.b@facs.com

FACS Project #PJ80246

Contents

List of Acronyms.......................................................1

Executive Summary..................................................2

Introduction.................................................................3

Scope of Work............................................................3

Site Characterization................................................3

Survey Methods.........................................................3

Regulations.................................................................6

Findings and Recommendations..........................9

Limitations.................................................................10

Appendix A: Asbestos Survey Summary, Sample Chain-of-Custody and Laboratory Results Report
Appendix B: Lead Paint Chip Summary, Lead Bulk Sample Chain-of-Custody, Laboratory Results Report, XRF Lead Testing Data and CDPH Form 8552
Appendix C: Site Drawing

Appendix D: Certifications of Personnel and Laboratories

www.forensicanalytical.com	Forensic Analytical Consulting Services

CUSD Cole ES – Exterior Hazardous Materials Survey for Repainting	1/31/2024	1 of 10

List of Acronyms

AIHA AL
Cal/OSHA CCR
CFR DOSH ELAP EPA FACS FALI HMS, Inc. LBP
ND NIOSH NIST PEL
RRP Rule

TTLC

American Industrial Hygiene Association Action Level
California Occupational Safety and Health Association Code of California Regulations
Code of Federal Regulation

Department of Occupational Safety and Health Environmental Laboratory Accreditation Program Environmental Protection Agency
Forensic Analytical Consulting Services, Inc. Forensic Analytical Laboratories, Inc.
Hazard Management Services, Inc. (now FACS, as of 9/1/18) Lead-Based Paint
None Detected

National Institute for Occupational Safety and Health National Institute of Science and Technology Permissible Exposure Limit
EPA Renovation, Repair and Painting Rule

Total Threshold Limit Concentration

www.forensicanalytical.com	Forensic Analytical Consulting Services

CUSD Cole ES – Exterior Hazardous Materials Survey for Repainting	1/31/2024	2 of 10

Executive Summary

Forensic Analytical Consulting Services, Inc. (FACS) was retained by Clovis Unified School District to perform a hazardous materials survey of exterior building surfaces at Cole Elementary School, located at 615 West Stuart Avenue in Clovis, California. The survey included suspect lead-containing paints or coatings and suspect asbestos-containing materials which may be impacted by the planned exterior repainting project at this site. A summary list of suspected asbestos-containing materials which were identified and sampled is included in Appendix A of this report. Appendix B of this report contains a data table listing all XRF test results, and the chain-of-custody and laboratory analysis report for any bulk lead sampling performed. The survey was performed on January 10, 2024.

Asbestos

Asbestos testing was performed on site to ensure that materials that may potentially be disturbed during the upcoming exterior painting project may be handled as “asbestos-free”. All the materials sampled were found to not contain asbestos by laboratory analysis. Please see the summary table in Appendix A for a complete listing of suspect materials sampled during this survey. Any suspect materials not included in this inspection must be assumed to be asbestos-containing materials until tested and proven not to contain asbestos.

FACS recommends that the results of this report be incorporated into any renovation plans provided for this project for informational purposes.

Lead-Based Paints

Lead-based paints or coatings have lead content at or above 1.00 mg/cm2, 5,000 parts per million or 0.5% by weight. The following painted component was found to be lead-based by XRF analysis:

•	Blue Paint on Stucco Wall Support – Covered Walkways

Lead-Containing Paints

A lead-containing paint or coating is defined as any detectable lead concentration at any level; there is no lower bound to lead content in the applicable regulations. Please refer to the XRF data table in Appendix A for specific results for tested items. Any XRF test results with a positive value, paints that were not tested during this survey, or any 0.00 mg/cm2 results which do not have corresponding verification by bulk sample analysis must be considered lead-containing.

Lead-Free Paints

Nine bulk samples were collected during this survey to verify XRF results of 0.00 mg/cm2. Of the verification samples collected, laboratory analysis indicates that the following paints or coatings may be handled as “lead-free”:

•      Beige paint on Stucco Wall – Wing 1 •      Beige paint on Stucco Wall – Wing 3
•	Blue paint on Metal Door Frame – Wing 2 •	Beige paint on Metal Louver Vent – Wing 1 •	Beige paint on Metal Truss Beam – Library •	Black paint on Metal Support Column –
Playground

•	Beige paint on Wood Wall – PRC 24
•	Blue paint on Metal Door Frame – Admin Building •	Beige paint on Stucco Wall – Wing 2
•	Blue paint on Wood Window Frame- PRC 30 •	White paint on Stucco Sofit – Pump House

www.forensicanalytical.com	Forensic Analytical Consulting Services

CUSD Cole ES – Exterior Hazardous Materials Survey for Repainting	1/31/2024	3 of 10

Introduction

Forensic Analytical Consulting Services, Inc. (FACS) was retained by Clovis Unified School District to perform a hazardous materials survey of exterior building surfaces at Cole Elementary School, located at 615 West Stuart Avenue in Clovis, California. The survey included suspect lead-containing paints or coatings and suspect asbestos-containing materials which may be impacted by the planned exterior repainting project at this site. The survey was performed on January 10, 2024.

Scope of Work

The purpose of this survey was to identify lead-based, lead-containing paints or coatings, and asbestos-containing materials which may be impacted by the planned exterior repainting of this school site. The visual inspection, XRF testing, bulk sampling, and survey documentation were performed by Sean Baker and Troy O’Connor. Mr. Baker is a California Department of Public Health (CDPH) Certified Lead Sampling Technician (#LRC-00009402) and Division of Occupational Safety and Health (DOSH) Certified Site Surveillance Technician (CSST #23-7487). Mr. O’Connor is an Asbestos Hazard Emergency Response Act (AHERA)-accredited Building Inspector. The survey was conducted under the direction and supervision of Chris Chipponeri, who is a CDPH Certified Lead Inspector / Assessor (#LRC-00000782) and DOSH Certified Asbestos Consultant (CAC #10-4633), as required by California regulations. The scope of the survey and the services provided by FACS included:

•	Performing a visual inspection of exterior building and structure surfaces for paints or coatings which may be impacted during the repainting project and suspect materials that may be disturbed;

•	Testing of paints and coatings using an XRF analyzer to determine lead content;

•	Collection of verification bulk samples as needed for analysis by flame atomic absorption spectrometry (AAS);

•	 Ensuring the technical quality of all work by using DOSH Certified Asbestos Consultants and Certified Site Surveillance Technicians;

•	Ensuring the technical quality of all work by using CDPH Certified Lead Sampling Technicians and Inspector/Risk Assessors;

•	Consolidating data and findings into a written report format.

Site Characterization

Cole Elementary School is a typical school site located in Clovis, California. The site contains permanent buildings and several portable classrooms. The permanent structures are wood framed on concrete with exterior stucco walls. The portable-type structures are metal-framed on concrete piers with wood wall panels. Only exterior surfaces were included in this survey.

Survey Methods

Visual Inspection

Exterior painted and coated surfaces which will be repainted were visually assessed during the course of the lead survey. The condition of all tested surfaces has been categorized as intact, fair or poor, to aid contractors in determining where lead remediation work may be required to facilitate preparatory work

www.forensicanalytical.com	Forensic Analytical Consulting Services

CUSD Cole ES – Exterior Hazardous Materials Survey for Repainting	1/31/2024	4 of 10

that may be needed during the repainting project. During this visual inspection, it was determined if any suspect materials would be disturbed by preparation activities.

All exterior areas were accessible during this survey. Interior areas will not be included in the repainting project and were not included in this survey.

Asbestos Inspection

Bulk Sample Collection

Bulk samples of identified homogeneous materials were collected in building areas that may be impacted by the planned painting activities to the best of FACS’ knowledge. Samples were collected of each separate homogeneous area. A homogeneous area is defined as a surfacing material, thermal system insulation, or miscellaneous material that is uniform in use, color and texture. Examples of homogeneous areas could include:

Vinyl floor tiles False ceiling panels
Drywall with joint compound Vinyl sheet flooring

The specific number of samples collected was determined by using the methods required by the Federal AHERA regulations (40 CFR, Part 763.86) as noted below:

1)	For Surfacing Material:
1,000 ft2 or less - collect 3 samples 1,001 to 5,000 ft2 - collect 5 samples 5,001 ft2 or greater - collect 7 samples

2)	For Thermal System Insulation:
“In a randomly distributed manner” - collect 3 samples 6 linear feet of patching or less - collect 1 sample
cementitious pipe fittings - “In a manner sufficient to determine”

3)	For all Miscellaneous Material:
Collect samples "In a manner sufficient to determine whether material is ACM (asbestos-containing material) or not ACM..."

The suspect ACMs were sampled using a knife, chisel, scraper, drill or other similar coring device suitable to the type of material sampled to cut through its entire thickness and to ensure that a cross-section of the material was obtained. The material was then placed in an appropriately labeled container that was sealed and submitted to SGS-Forensic Laboratories for analysis. A unique sample number (e.g. PJ80246-01A) was assigned to each sample.

Bulk samples will be retained by the laboratory for one month unless otherwise instructed. After this period, the samples will be disposed of appropriately.

Bulk Sample Analysis

A total of three (3) bulk samples were collected from a total of one (1) suspect material. Bulk samples were analyzed by SGS-Forensic Laboratories (SGS-FL) in Hayward, California. SGS-FL is accredited by the California Department of Public Health (CDPH) Environmental Laboratory Accreditation Program (ELAP) and the National Institute of Science and Technology's (NIST) National Voluntary Laboratory Accreditation Program (NVLAP). SGS-FL participates in the National Institute for Occupational Safety

www.forensicanalytical.com	Forensic Analytical Consulting Services

CUSD Cole ES – Exterior Hazardous Materials Survey for Repainting	1/31/2024	5 of 10

and Health (NIOSH) Proficiency Analytical Testing Program and has substantial experience in the analysis of asbestos.

All samples were analyzed using Polarized Light Microscopy with Dispersion Staining (PLM/DS) techniques in accordance with the methodology approved by the U.S. Environmental Protection Agency (EPA). The percentage of asbestos present in the samples was determined on the basis of a visual area estimation. The EPA defines asbestos-containing materials (ACM) as any material containing more than one percent (1%) asbestos as determined using the method specified in Appendix A, Subpart F, 40 CFR Part 763, Section 1, Polarized Light Microscopy (PLM). 40 CFR Part 763 identifies the lower limit of reliable quantification for asbestos using the PLM method as approximately one percent (1%) by volume. Regulations in California (CAL/OSHA Title 8 CCR 1529) define asbestos-containing construction materials (ACCM) as those materials having asbestos content of greater than one tenth of one percent (> 0.1%); therefore, for the purpose of this survey, any amount of asbestos detected will be considered positive. In addition to the percentages, the types of asbestos minerals are also reported. The PLM method is the standard method used to analyze asbestos bulk samples.

When "None Detected" (ND) appears in the laboratory results, it should be interpreted as meaning asbestos was not observed in the sample material.

Lead Inspection

The client-defined lead inspection was conducted in accordance with the CDPH Lead-Related Construction Program and modeled upon the sampling protocol described in “Chapter 7: Lead Based Paint Inspection” of the HUD Guidelines for the Evaluation and Control of Lead-Based Paint Hazards in Housing (1997 Revision.)

Cal/OSHA, in Title 8 California Code of Regulations (CCR) Section 1532.1, Lead in Construction Standard which implements California Labor Code 8716-6717, regulates all construction work were an employee may be occupationally exposed to lead. Paint or materials with any detectable lead are considered lead-containing by Cal/OSHA.

For purposes of this report, materials containing lead shall be defined as materials that XRF testing has determined contain a lead content at or above 0.01 mg/cm2, or 0.00 mg/cm2 readings which have not been confirmed with laboratory analysis of bulk samples. For bulk samples, lead containing materials are defined as those paints or coatings with a lead content at or above the reporting limit for the sample.

XRF Testing Methodology

Surfaces and components were surveyed for lead content utilizing a portable X-ray fluorescence (XRF) analyzer, SciAps X-550Pb, serial number 01149. The XRF analyzer contains an electronically-powered source which bombards tested surfaces with X-rays and gamma rays. This external energy source excites any lead atoms within the tested paint or coating, causing their atoms to emit X-ray photons with a characteristic energy profile. The instrument analyzes the emitted energy to identify and quantify the amount of lead in the tested paint or coating, with lead content reported in milligrams per square centimeter.

Testing combinations of homogeneous components in one area are representative of similar components found in other areas with similar construction and painting histories. During this survey, the inspector visually identified the painted or coated component to test, an XRF reading was collected, and the reading was documented in the XRF data table contained in Appendix A. For each test reading, the data table identifies the room equivalent/space designation, the tested component name, the substrate material, the sample location, paint/coating color, condition assessment, and the XRF result expressed as lead content by weight in milligrams per square centimeter (mg/cm2).

www.forensicanalytical.com	Forensic Analytical Consulting Services

CUSD Cole ES – Exterior Hazardous Materials Survey for Repainting	1/31/2024	6 of 10

Bulk Sample Methodology

XRF testing performed during this survey was used to determine which paints or coatings at the site have detectable concentrations of lead, and to determine which paints or coatings at the site are lead-based paint. Cal/OSHA does not accept XRF test results for use in determining that a paint or coating does not contain lead. Cal/OSHA requires laboratory analysis of a bulk sample to classify a paint or coating as lead-free. Bulk samples may have been collected to confirm some of the 0.00 mg/cm² XRF test readings obtained during this survey, particularly for non-intact surfaces for which preparatory work may be needed that may create worker exposures to lead. If the preponderance of XRF testing indicates lead-containing paints or coatings are present, verification of 0.00 mg/cm2 results with bulk sampling will be limited as it will not change the repainting project requirements.

For bulk samples that may have been collected during this survey, samples were collected by a CDPH Lead Sampling Technician (under the direction of an Inspector/Assessor) or by an Inspector/Assessor using a knife, chisel or scraper. Such samples were logged on a chain-of-custody and shipped via FedEx to SGS – Forensic Laboratories (SGS) for analysis of lead content using flame atomic absorption spectroscopy (AAS). SGS is accredited by the American Industrial Hygiene Association’s Environmental Lead Laboratory Accreditation Program for the analysis of bulk lead paint chip samples. Analysis results are expressed as percent by weight. Paints or coatings with a sample result listed as less than the reporting limit for the sample may be handled as not containing a detectable concentration of
lead.

Regulations

Background

Asbestos is the name of a class of magnesium-silicate minerals that occur in fibrous form. Minerals that are included in this group are chrysotile, crocidolite, amosite, anthophyllite asbestos, tremolite asbestos, and actinolite asbestos. Although the chrysotile minerals are the most common type of asbestos found in the construction industry, all types of asbestos are regulated in the same manner. Asbestos has been used in more than 3,000 different building materials. Asbestos was added to building materials to: increase fire-resistance, insulate against heat, cold and sound, resist corrosion, and increase tensile strength. Common building materials that may contain asbestos include but are not limited to the following: floor tile, resilient sheet flooring, ceiling tile, mastics, roofing materials, fireproofing, acoustical treatments, wallboard, pipe and boiler insulations. Adverse health effects have been associated with the inhalation of airborne asbestos. However, asbestos fibers that are tightly bound in the building material, may not represent an exposure hazard, unless disturbed in such a way that releases airborne fibers (i.e., cutting, drilling, sanding, and other abrasive methods).

Building Surveys

The following is a summary of some current Federal and California State regulations which contain requirements related to the performance of building surveys for asbestos. These summaries are not intended to be all inclusive and do not contain every aspect of the regulations discussed.

U.S. EPA National Emission Standard for Hazardous Air Pollutants (NESHAPs), 40 CFR Part 61

Under the NESHAPs regulation, no visible emissions are allowed during building demolition or renovation activities which involve regulated asbestos-containing materials. For this reason, all buildings must be surveyed for asbestos-containing materials prior to demolition or renovation. The EPA, CARB, and/or the local Air Quality Management District which implements EPA actions, must be notified prior to any building demolition even if no asbestos-containing materials are present.

www.forensicanalytical.com	Forensic Analytical Consulting Services

CUSD Cole ES – Exterior Hazardous Materials Survey for Repainting	1/31/2024	7 of 10

Regulated asbestos-containing material (RACM) is defined as a) any friable material with an asbestos content of greater than one percent, or b) any non-friable material with asbestos content of greater than one percent that will, or could, become friable.

Asbestos Hazard Emergency Response Act (AHERA), 40 CFR Part 763, Subpart E

AHERA requires performance of asbestos surveys and the development of Asbestos Management Plans for all primary and secondary schools in the United States. Although this regulation applies to primary and secondary schools only, the procedures mandated under AHERA are considered the industry standard and are applied to all surveys performed by FACS unless otherwise specified by the building owner.

Worker Protection

California Assembly Bill AB3713, Health and Safety Code Division 20, Chapter 10.4, Section 25915-25924

The state of California has enacted legislation that requires building owners, employers, lessees, etc. to notify tenants, employees and contractors of the presence of asbestos in both friable and non-friable forms. In addition, preventive maintenance activities must be developed and communicated to these parties. Notification is required 15 days after the identification of ACM in the building, and annually thereafter.

Occupational Safety and Health Administration (OSHA) 29 CFR 1926.1101 and 8 CCR 1529

The Federal and State Occupational Safety and Health Administrations (OSHA) require employers to implement specific work practices which protect workers from airborne asbestos exposure.

Building materials which contain even low levels of asbestos (<1%) can potentially generate significant concentrations of airborne asbestos fibers when disturbed. Therefore, control measures should be instituted which adequately address worker health and safety during planned renovation or demolition activities involving these materials. Cal/OSHA defines asbestos-containing construction materials as those materials having greater than one tenth of one percent asbestos (>0.1%). As stated previously, there is currently no viable method to accurately quantify asbestos at this level.

Hazardous Waste

Building materials reported to contain less than one percent (<1%) of asbestos are not considered hazardous by the U.S. EPA, and hence, may not require removal and disposal prior to demolition or renovation. Regulations may vary, however, between regional air quality management districts and/or other state agencies responsible for implementing EPA's rules. Therefore, local agencies should be contacted for specific ACM definitions and handling requirements. Cal/OSHA may also require special packaging and labeling on containers with asbestos-containing construction materials.

Composite sampling, which may potentially reduce the total asbestos content of the material, is only permitted when sampling joint compound, tape, and gypsum wallboard according to EPA’s Asbestos NESHAP Clarification Regarding Analysis of Multi-Layered Systems (40 CFR Part 61 FRL-4821-7).

Lead

Cal/OSHA Lead (8 CCR 1532.1) & CDPH (Title 17)

If existing paints or coatings will be impacted, a project should be considered regulated by Cal/OSHA as lead-related construction (8 CCR 1532.1).

www.forensicanalytical.com	Forensic Analytical Consulting Services

CUSD Cole ES – Exterior Hazardous Materials Survey for Repainting	1/31/2024	8 of 10

A contractor who has employees that may be occupationally exposed to lead during this project must perform an initial determination regarding worker exposures to lead, which may be based on personal air monitoring at the start of the project, prior employee monitoring from the past 12 months under workplace conditions closely resembling the current project, or objective data demonstrating that exposures will not exceed the Cal/OSHA action level (30 micrograms per cubic meter of air). It is the contractor’s responsibility to conduct their initial determination and comply with any relevant Cal/OSHA requirements.

Workers disturbing existing paints or coatings during a project must have lead awareness or action level training depending on the initial exposure determination and lead-safe work practices must be used. Disturbance of lead-containing paints or coatings must be performed within a contained area to prevent the spread and build-up of lead dust in order to comply with CDPH requirements. HEPA vacuums, dustless tools or shrouds, and/or intact removal of components should be employed to minimize lead dust generation and properly cleanup work areas following disturbance to lead-containing materials during a project. Waste generated during disturbance to lead-containing materials must be profiled in a hazardous waste determination to ascertain proper disposal requirements.

If the initial determination or initial exposure monitoring shows that workers impacting lead can be expected to be or are shown to be exposed to lead above the Cal/OSHA permissible exposure level (50 micrograms per cubic meter of air) workers and supervisors must have the requisite training and CDPH lead worker or supervisor certification.

EPA Renovation, Repair and Painting Rule Requirements

The EPA’s Renovation, Repair, and Painting (RRP) rule applies to disturbance of lead-based paints at child-occupied facilities constructed before 1978. In the context of the RRP rule, child-occupied facility is defined as being visited by the same child under the age of 6 on two or more days per week for at least 3 hours per visit with a cumulative annual total of 60 hours.

If more than 6 square feet of painted or coated components with lead-based paint is to be disturbed during this project at interior areas, or 20 square feet or more at exterior areas, the work (and this project) would be regulated under the RRP rule. In addition, the RRP rule is triggered if windows have “wet-applied” lead-based paint and one window will be removed.

Firms paid to perform RRP-covered work must be registered with the US EPA RRP program; this requirement applies to a General Contractor, Construction Management firm, or other entity contracting for and overseeing the work, even if the actual RRP-covered work is performed by a sub-contractor or other firm. Firms may not bid on an RRP-covered project without first obtaining firm certification, and contracts for RRP-covered projects may not be awarded to firms without firm certification. Proof of RRP firm certification must be submitted to the Owner.

The RRP rule requires distribution of the EPA’s Renovate Right lead hazard information pamphlet before the start of covered work to occupants, building owners, and parents of children in child-occupied facilities. This may be fulfilled by distributing individual copies of the pamphlet, or publicly posting the pamphlet at accessible locations at the project site. The contractor must document how they have fulfilled this requirement and must submit this proof to the Owner.

In addition to any Cal/OSHA or CDPH required training for all lead workers, at least one such supervisory employee working on the project must have received EPA-approved RRP training and possess a valid Certified Renovator certification. The Certified Renovator may be provided by the firm directly performing the work covered by the RRP rule or by the controlling firm if the work is sub-contracted; in such cases, both firms are not required to provide a Certified Renovator. Other workers disturbing lead during an RRP project may receive on-the-job training from a Certified Renovator on the RRP Rule and

www.forensicanalytical.com	Forensic Analytical Consulting Services

CUSD Cole ES – Exterior Hazardous Materials Survey for Repainting	1/31/2024	9 of 10

its requirements or may themselves be Certified Renovators. Proof of Certified Renovator certification and training of other workers must be submitted to the Owner

The RRP rule also requires the use of lead-safe work practices. Work area containment must be used, which is fulfilled by using drop sheets, and vertical barriers if needed, to prevent dust and debris from leaving the work area. Wet-work methods should be used to minimize airborne lead dust generation. Open-flame burning, use of heat guns at greater than 1,100 degrees Fahrenheit, and use of power tools without HEPA exhaust controls are prohibited work practices under the RRP rule. High-pressure power washing of surfaces that dislodges paint would require capture and filtering of all water; this method should be avoided to limit the potential for creating a lead-hazard during the project. Following the lead disturbance, surfaces must be thoroughly cleaned to remove all dust and debris, and the contractor must perform and document their cleaning verification wipe sampling if performing work at interior locations.

Additional requirements exist within the rule. It is recommended that Clovis Unified School District ensure contractors disturbing paints are thoroughly familiar with the requirements of the rule.

Findings and Recommendations

Forensic Analytical Consulting Services, Inc. (FACS) was retained by Clovis Unified School District to perform an asbestos and lead survey for an upcoming exterior painting project at Cole Elementary School, located at 615 West Stuart Avenue in Clovis, California.

Asbestos

All the materials sampled were found to not contain asbestos by laboratory analysis. Please see the summary table in Appendix A for a complete listing of suspect materials sampled during this survey.

Any suspect materials not included in this inspection must be assumed to be asbestos-containing materials until tested and proven not to contain asbestos.

Lead-Based Paints

Lead-based paints or coatings have lead content at or above 1.00 mg/cm2, 5,000 parts per million or 0.5% by weight. The following painted component was found to be lead-based by XRF analysis:

•	Blue Paint on Stucco Wall Support – Covered Walkways

Lead-Containing Paints

A lead-containing paint or coating is defined as any detectable lead concentration at any level; there is no lower bound to lead content in the applicable regulations. Please refer to the XRF data table in Appendix A for specific results for tested items. Any XRF test results with a positive value, paints that were not tested during this survey, or any 0.00 mg/cm2 results which do not have corresponding verification by bulk sample analysis must be considered lead-containing.

Lead-Free Paints

Nine bulk samples were collected during this survey to verify XRF results of 0.00 mg/cm2. Of the verification samples collected, laboratory analysis indicates that the following paints or coatings may be handled as “lead-free”:

•      Beige paint on Stucco Wall – Wing 1 •      Beige paint on Stucco Wall – Wing 3

•	Blue paint on Metal Door Frame – Wing 2 •	Beige paint on Metal Louver Vent – Wing 1

www.forensicanalytical.com	Forensic Analytical Consulting Services

CUSD Cole ES – Exterior Hazardous Materials Survey for Repainting	1/31/2024	10 of 10

•	Beige paint on Metal Truss Beam – Library •	Black paint on Metal Support Column –
Playground
•	Beige paint on Wood Wall – PRC 24

•	Blue paint on Metal Door Frame – Admin Building •	Beige paint on Stucco Wall – Wing 2
•	Blue paint on Wood Window Frame- PRC 30 •	White paint on Stucco Sofit – Pump House

Limitations

This investigation is limited to the conditions and practices observed and information made available to FACS. The methods, conclusions and recommendations provided are based on FACS’ judgment, expertise and the standard of practice for professional service. They are subject to the limitations and variability inherent in the methodology employed. As with all environmental investigations, this investigation is limited to the defined scope and does not purport to set forth all hazards, nor indicate that other hazards do not exist.

Please do not hesitate to contact our office at 559-436-0277 with any questions or concerns. Thank you for the opportunity to assist Clovis Unified School District with promoting workers, staff and student safety and a healthy environment.

Respectfully,
FORENSIC ANALYTICAL

Sean Baker
Environmental Health Specialist, Fresno Cal/OSHA CSST # 23-7487
CDPH LRC-00009402

www.forensicanalytical.com

Reviewed by:
FORENSIC ANALYTICAL

Chris Chipponeri
Local Director, Central Valley Offices Cal/OSHA CAC #10-4633
CDPH I/A #LRC-00000782

Forensic Analytical Consulting Services

CUSD Cole ES – Exterior Hazardous Materials Survey for Repainting	1/31/2024	Appendix A

Appendix A

Asbestos Survey Summary, Sample Chain-of-Custody and Laboratory Results Report

Asbestos Survey Summary (Lab Report #B355666)
Clovis Unified School District – Cole Elementary School – Exterior Repainting Survey Date: January 10, 2024
	
Sample Numbers
	Material Description
	Location(s) of Material
	Material Number
	
Asbestos Content (percent)
	NESHAP Category
	Approximate Quantity

01A
	
Stucco
	
Admin Building
	
1
	Layer: Grey Cementitious Material: None Detected Layer: Off-White Cementitious Material: None Detected Layer: Paint: None Detected
	
NA
	
NA

01B
	
Stucco
	
Pump House
	
1
	Layer: Grey Cementitious Material: None Detected Layer: Off-White Cementitious Material: None Detected Layer: Paint: None Detected
	
NA
	
NA

01C
	
Stucco
	
Wing 2
	
1
	Layer: Grey Cementitious Material: None Detected Layer: Off-White Cementitious Material: None Detected Layer: Paint: None Detected
	
NA
	
NA

www.forensicanalytical.com	Forensic Analytical Consulting Services

Final Report

Bulk Asbestos Analysis
(EPA Method 40CFR, Part 763, Appendix E to Subpart E and EPA 600 R 93-116, Visual Area Estimation NVLAP Lab Code: 101459 0

FACS - Fresno Tyler Faison 21228 Cabot Blvd.

Hayward, CA 94545

Client ID: Report Number: Date Received: Date Analyzed: Date Printed: First Reported:

FR09 B355666 01/12/24 01/19/24 01/19/24 01/19/24

Job ID/Site: PJ80246; Clovis Unified School District 615 West Stuart Avenue Clovis CA 93611	 SGSFL Job ID:	FR09 Total Samples Submitted: 3
Date(s) Collected: 01/02/2024	Total Samples Analyzed:	3

Sample ID

PJ80246-01A
Layer: Grey Cementitious Material Layer: White Cementitious Material Layer: Paint

Lab Number

12722764

Asbestos Type

Percent in Layer

ND ND ND

Asbestos Type

Percent in Layer

Asbestos Type

Percent in Layer

Total Composite Values of Fibrous Components:	Asbestos ND) Cellulose (Trace)

PJ80246-01B	12722765

Layer: Grey Cementitious Material	ND Layer: White Cementitious Material	ND Layer: Paint	ND

Total Composite Values of Fibrous Components:	Asbestos ND) Cellulose (Trace)

PJ80246-01C	12722766

Layer: Grey Cementitious Material                                                                ND Layer: Paint                                                                                                     ND

Total Composite Values of Fibrous Components:	Asbestos ND) Cellulose (Trace)

Maria Cosper, Laboratory Supervisor, Hayward Laboratory
Note: Limit of Quantification ('LOQ') = 1%. 'Trace' denotes the presence of asbestos below the LOQ. 'ND' = 'None Detected'. Analytical results and reports are generated by SGS Forensic Laboratories (SGSFL) at the request of and for the exclusive use of the person or entity (client) named on such report. Results, reports or copies of same will not be released by SGSFL to any third party without prior written request from client. This report applies only to the sample(s) tested. Supporting laboratory documentation is available upon request. This report must not be reproduced except in full, unless approved by SGSFL. The client is solely responsible for the use and interpretation of test results and reports requested from SGSFL. This report must not be used by the client to claim product endorsement by NVLAP or any other agency of the U.S. Government. SGSFL is not able to assess the degree of hazard resulting from materials analyzed. SGS Forensic Laboratories reserves the right to dispose of all samples after a period of thirty (30) days, according to all state and federal guidelines, unless otherwise specified. All samples were received in acceptable condition unless otherwise noted.

Page 1 of 1 3777 Depot Road, Suite 409, Hayward, CA 94545 | Phone: 510.887.8828 / 800.827.3274 Fax: 510.887.4218 | https://falaboratories.sgs.com

CUSD Cole ES – Exterior Hazardous Materials Survey for Repainting	1/31/2024	Appendix B

Appendix B
Lead Paint Chip Summary, Lead Bulk Sample Chain-of-Custody, Laboratory Results Report, XRF Lead Testing Data and CDPH Form 8552

LEAD PAINT CHIP SUMMARY TABLE
Clovis Unified School District – Cole Elementary School – Exterior Repainting Survey Date: January 10, 2024 - Lab Report Numbers: M256881

Sample Number

Component Location

Component

Color

Substrate
			Analytical Results (weight percent of lead)

Pb01
	
Wing 1
	
Wall
		
Beige
			
Stucco
		
< 0.007

Pb02
	
Wing 3
	
Wall
		
Beige
			
Stucco
		
< 0.007

Pb03
	
Wing 2
	
Door Frame
		
Blue
			
Metal
		
< 0.006

Pb04
	
Wing 1
	
Louver Vent
	
Beige
		
Metal
		
< 0.006

Pb05
	
Library
	
Trusit Beam
		
Beige
			
Metal
		
< 0.006

Pb06
	
Playground
	
Support Column
		
Black
			
Metal
		
< 0.007

Pb07
	
PCR 24
	
Wall
	
Beige
		
Wood
		
< 0.007

Pb08
	
Admin Building
	
Door Frame
		
Blue
			
Metal
		
< 0.006

Pb09
		
Wing 2
	
Wall
		
Beige
			
Stucco
		
< 0.007

Pb010
		
PCR 30
	
Window Frame
		
Blue
			
Wood
		
<0.007

Pb11
		
Covered Walkway
	
Wall
		
Blue
			
Stucco
		
0.010

Pb12
		
Pump House
	
Sofit
		
White
			
Stucco
		
<0.006

www.forensicanalytical.com	Forensic Analytical Consulting Services

Final Report

Metals Analysis of Paints (AIHA-LAP, LLC Accreditation, Lab ID #101762)

FACS - Fresno Tyler Faison 21228 Cabot Blvd.

Hayward, CA 94545

Job ID / Site: PJ80246; Clovis Unified School District 615 West Stuart Avenue Clovis CA 93611

Client ID: Report Number: Date Received: Date Analyzed: Date Printed: First Reported:

SGSFL Job ID:

FR09 256881
01/12/24 01/17/24 01/19/24 01/19/24

FR09

Date(s) Collected: 1/10/24                                                                                                                      Total Samples Submitted: 12 Total Samples Analyzed:     12

Sample Number

PJ80246-PB01 PJ80246-PB02 PJ80246-PB03 PJ80246-PB04 PJ80246-PB05 PJ80246-PB06 PJ80246-PB07 PJ80246-PB08 PJ80246-PB09 PJ80246-PB10 PJ80246-PB11
PJ80246-PB12

Lab Number

30933550 30933551 30933552 30933553 30933554 30933555 30933556 30933557 30933558 30933559 30933560
30933561

Analyte	Result

Pb	< 0.007 Pb	< 0.007 Pb	< 0.006 Pb	< 0.006 Pb	< 0.006 Pb	< 0.007 Pb	< 0.007 Pb	< 0.006 Pb	< 0.007 Pb	< 0.007 Pb              0.010
Pb	< 0.006

Result	Reporting Units            Limit

wt%	0.007 wt%	0.007 wt%	0.006 wt%	0.006 wt%	0.006 wt%	0.007 wt%	0.007 wt%	0.006 wt%	0.007 wt%	0.007 wt%	0.006
wt%	0.006

Method Reference

EPA 3050B/7000B EPA 3050B/7000B EPA 3050B/7000B EPA 3050B/7000B EPA 3050B/7000B EPA 3050B/7000B EPA 3050B/7000B EPA 3050B/7000B EPA 3050B/7000B EPA 3050B/7000B EPA 3050B/7000B
EPA 3050B/7000B

* The Reporting Limit represents the lowest amount of analyte that the laboratory can confidently detect in the sample, and is not a regulatory level. The Units for the Reporting Limit are the same as the Units for the Final Results.

Kevin Poon, Laboratory Supervisor, Hayward Laboratory

Analytical results and reports are generated by SGS Forensic Laboratories at the request of and for the exclusive use of the person or entity (client) named on such report. Results, reports or copies of same will not be released by SGS Forensic Laboratories to any third party without prior written request from client. This report applies only to the sample(s) tested. Supporting laboratory documentation is available upon request. This report must not be reproduced except in full, unless approved by SGS Forensic Laboratories. The client is solely responsible for the use and interpretation of test results and reports requested from SGS Forensic Laboratories. SGS Forensic Laboratories is not able to assess the degree of hazard resulting from materials analyzed. SGS Forensic Laboratories reserves the right to dispose of all samples after a period of thirty (30) days, according to all state and federal guidelines, unless otherwise specified. Any modifications that have been made to referenced test methods are documented in SGS Forensic Laboratories' Standard Operating Procedures Manual. Sample results have not been blank corrected. Quality control and sample receipt condition were acceptable unless otherwise noted.
Note*Sampling data used in this report was provided by the client as noted on the associated chain of custody form.

Page 1 of 1 3777 Depot road, Suite 409, Hayward, CA 94545 | Phone: 510.887.8828 / 800.827.3274 Fax: 510.887.4218 | https://falaboratories.sgs.com

SURVEY FOR LEAD BASED PAINT Clovis Unified School District

Site Name:

Address:

Cole Elementary School

615 West Stuart Ave., Clovis, CA

Date:

FACS Job #:

1/10/24

PJ80246

Start Time:	1007

End Time:	1152

Calibration:

Calibration:

1.04 = 1.02

1.04 = 1.03

1.04 = 1.01

1.04 = 1.05

1.04 = 1.02

1.04 = 1.08

Technician:

Inspector/Assessor:

Sean Baker / Troy O’Connor

Chris Chipponeri

SciAps X-550Pb	Readings in red are lead-based.

Condition Codes:
I = Intact, F = Fair, P = Poor

No.	Sample Location

1.	Exterior - Admin Building - South Side 2.	Exterior - Admin Building - East Side 3.	Exterior - Admin Building - East Side 4.	Exterior - Admin Building - East Side 5.	Exterior - Admin Building - East Side 6.	Exterior - Portacio - East Side
7.	Exterior - Portacio - East side 8.	Exterior - Portico - North Side 9.	Exterior - Portico - North Side
10. Exterior - Admin Building - West side 11. Exterior - Admin Building - West side 12. Exterior - Admin Building - West side 13. Exterior - Admin Building - West side 14. Exterior - Admin Building - West side 15. Exterior - Admin Building - West side 16. Exterior - Admin Building - West side
17. Exterior – Classroom Wing 1 – South Side 18. Exterior – Classroom Wing 1 – South Side
19. Exterior – Classroom Wing 1 – South Side

Color	Substrate

Beige                        Stucco Blue                          Metal Blue                          Metal Beige                        Stucco
Beige	Metal Blue                         Stucco
White	Metal Blue	Metal Blue	Metal
Beige                        Stucco Blue                          Metal Blue                          Metal Blue                          Metal Blue                          Metal White                        Stucco
Beige	Metal Beige                        Stucco Beige	Metal
Beige	Metal

Component

Wall Door Frame
Door Wall
Conduit Pipe Portico Flashing Support Pole Support Pole Wall
Support Pole Door Frame Door Drainpipe Portico
Window Frame Wall
Window Frame

Louver

Condition

I I I I I I I I I I I I I I I I I I
I

XRF Result (mg/cm2)

0.00 0.00 0.00 0.00 0.00 0.00 0.00 4.32 7.63 0.00 7.97 0.00 0.00 0.00 0.02 0.00 0.00 0.00
0.00

SURVEY FOR LEAD BASED PAINT Clovis Unified School District

Site Name:

Address:

Cole Elementary School

615 West Stuart Ave., Clovis, CA

Date:

FACS Job #:

1/10/24

PJ80246

Start Time:	1007

End Time:	1152

Calibration:

Calibration:

1.04 = 1.02

1.04 = 1.03

1.04 = 1.01

1.04 = 1.05

1.04 = 1.02

1.04 = 1.08

Technician:

Inspector/Assessor:

Sean Baker / Troy O’Connor

Chris Chipponeri

SciAps X-550Pb	Readings in red are lead-based.

Condition Codes:
I = Intact, F = Fair, P = Poor

No.	Sample Location

20. Exterior – Classroom Wing 1 – South Side 21. Exterior – Classroom Wing 1 – South Side 22. Exterior – Classroom Wing 1 – East Side 23. Exterior – Classroom Wing 1 – East Side 24. Exterior – Classroom Wing 1 – North Side 25. Exterior – Classroom Wing 1 – North Side 26. Exterior – Classroom Wing 1 – North Side 27. Exterior – Classroom Wing 1 – North Side 28. Exterior – Classroom Wing 1 – North Side 29. Exterior – Classroom Wing 1 – West Side 30. Exterior – Classroom Wing 2 – South Side 31. Exterior – Classroom Wing 2 – South Side 32. Exterior – Classroom Wing 2 – South Side 33. Exterior – Classroom Wing 2 – South Side

34. Exterior – Classroom Wing 2 – South Side 35. Exterior – Classroom Wing 2 – South Side 36. Exterior – Classroom Wing 2 – South Side 37. Exterior – Classroom Wing 2 – West Side
38. Exterior – Classroom Wing 2 – North Side

Color	Substrate

Blue	Metal Blue	Metal Blue	Metal
White	Porcelain Beige                        Stucco Beige                         Metal
Blue                          Metal Blue                          Metal Blue                          Metal Beige                        Stucco Beige                        Stucco Beige                         Metal Blue                          Metal Blue                          Metal

Blue                          Metal Beige                         CMU Beige                         Wood Blue                          Wood
Blue	Stucco

Component

Door Frame Door Handrail Sink Wall
Louver Vent Flashing Door Frame Door Wall Wall
Window Frame Door Frame
Door Electrical Pannel

Wall Wall
Door Frame

Flashing

Condition

I I I I I I I I I I I I I I

I I I F
I

XRF Result (mg/cm2)

0.00 0.00 0.00 0.02 0.00 0.12 0.01 0.00 0.00 0.00 0.00 0.00 0.00 0.00

0.00 0.00 0.00 0.00
0.00

SURVEY FOR LEAD BASED PAINT Clovis Unified School District

Site Name:

Address:

Cole Elementary School

615 West Stuart Ave., Clovis, CA

Date:

FACS Job #:

1/10/24

PJ80246

Start Time:	1007

End Time:	1152

Calibration:

Calibration:

1.04 = 1.02

1.04 = 1.03

1.04 = 1.01

1.04 = 1.05

1.04 = 1.02

1.04 = 1.08

Technician:

Inspector/Assessor:

Sean Baker / Troy O’Connor

Chris Chipponeri

SciAps X-550Pb	Readings in red are lead-based.

Condition Codes:
I = Intact, F = Fair, P = Poor

No.	Sample Location

39. Exterior – Classroom Wing 2 – North Side 40. Exterior – Classroom Wing 2 – North Side 41. Exterior – Classroom Wing 2 – North Side 42. Exterior – Classroom Wing 2 – North Side 43. Exterior – Classroom Wing 2 – North Side 44. Exterior – Classroom Wing 3 – South Side 45. Exterior – Classroom Wing 3 – South Side 46. Exterior – Classroom Wing 3 – South Side 47. Exterior – Classroom Wing 3 – South Side 48. Exterior – Classroom Wing 3 – South Side

49. Exterior – Classroom Wing 3 – South Side 50. Exterior – Portico – East Side
51. Exterior – Classroom Wing 3 – East Side 52. Exterior – Classroom Wing 3 – North Side 53. Exterior – Classroom Wing 3 – North Side

54. Exterior – Classroom Wing 3 – West Side 55. Exterior – Classroom Wing 3 – West Side
56. Baseball Field 1 – East Side

Color	Substrate

Blue	Metal Blue                         Stucco
Beige	Stucco Beige                         Metal Beige                         Metal Beige	Stucco
Blue                          Metal Blue                          Metal Beige                         Metal Beige                        Stucco

Beige                         Metal Blue                          Metal
Beige	Stucco Beige                         Metal Beige	Stucco

Grey                          Metal Beige                        Stucco
Green	Wood

Component

Flashing Sofit Wall
Louver Vent Window Frame Wall
Door Frame Door
Window Frame

Sofit Electrical Pannel

Support Pole Wall
Conduit Cover

Wall Drinking Fountain

Wall

Back Stop

Condition

I I I I I I I I I I

I I I I I

I I
I

XRF Result (mg/cm2)

0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00

0.01 3.18 0.00 0.00 0.00

0.00 0.00
0.00

SURVEY FOR LEAD BASED PAINT Clovis Unified School District

Site Name:

Address:

Cole Elementary School

615 West Stuart Ave., Clovis, CA

Date:

FACS Job #:

1/10/24

PJ80246

Start Time:	1007

End Time:	1152

Calibration:

Calibration:

1.04 = 1.02

1.04 = 1.03

1.04 = 1.01

1.04 = 1.05

1.04 = 1.02

1.04 = 1.08

Technician:

Inspector/Assessor:

Sean Baker / Troy O’Connor

Chris Chipponeri

SciAps X-550Pb	Readings in red are lead-based.

Condition Codes:
I = Intact, F = Fair, P = Poor

No.	Sample Location

57. Baseball Field 2 – South Side 58. Baseball Field 3 – South Side
59. Exterior – Classroom 18-21 – North Side 60. Exterior – Classroom 18-21 – North Side 61. Exterior – Classroom 18-21 – North Side 62. Exterior – Classroom 18-21 – North Side 63. Exterior – Classroom 18-21 – West Side 64. Exterior – Classroom 18-21 – West Side 65. Exterior – Classroom 18-21 – South Side 66. Exterior – Classroom 18-21 – South Side 67. Exterior – Classroom 18-21 – South Side 68. Exterior – Classroom 18-21 – South Side 69. Exterior – Classroom 18-21 – South Side 70. Exterior – Library – West Side
71. Exterior – Library – West Side 72. Exterior – Library – West Side 73. Exterior – Library – West Side 74. Exterior – Library – West Side
75. Exterior – Library – North Side

Color	Substrate

Green	Wood Blue                          Metal Blue                          Metal
Beige	Stucco Beige                         Metal Beige                         Metal Beige	Stucco
Blue                          Metal Beige                         Metal Beige                         Metal Blue                          Metal Blue                          Metal Beige                         Metal Beige                         Metal Beige                         Metal Beige                         Metal Beige                        Stucco Blue                          Metal
Beige	Metal

Component

Back Stop Bleachers Drainpipe Wall
Window Frame Window Casing Wall Flashing Sofit
Support Beam Door Frame Door
Window Frame Support Beam Window Frame Window Casing Wall Flashing
Drainpipe

Condition

I I I I I I I I I I I I I I I I I I
I

XRF Result (mg/cm2)

0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00
0.00

SURVEY FOR LEAD BASED PAINT Clovis Unified School District

Site Name:

Address:

Cole Elementary School

615 West Stuart Ave., Clovis, CA

Date:

FACS Job #:

1/10/24

PJ80246

Start Time:	1007

End Time:	1152

Calibration:

Calibration:

1.04 = 1.02

1.04 = 1.03

1.04 = 1.01

1.04 = 1.05

1.04 = 1.02

1.04 = 1.08

Technician:

Inspector/Assessor:

Sean Baker / Troy O’Connor

Chris Chipponeri

SciAps X-550Pb	Readings in red are lead-based.

Condition Codes:
I = Intact, F = Fair, P = Poor

No.	Sample Location

76. Exterior – Library – North Side 77. Exterior – Library – East Side 78. Exterior – Library – East Side 79. Exterior – Library – East Side
80. Exterior – Library at Dinking Fountain – East Side 81. Exterior – Classroom 13-17 – North Side
82. Exterior – Classroom 13-17 – North Side 83. Exterior – Classroom 13-17 – North Side 84. Exterior – Classroom 13-17 – North Side 85. Exterior – Classroom 13-17 – South Side 86. Exterior – Classroom 13-17 – South Side 87. Exterior – Classroom 13-17 – South Side 88. Exterior – MPR Building – East Side
89. Exterior – MPR Building – East Side 90. Exterior – MPR Building – East Side 91. Exterior – MPR Building – North Side 92. Exterior – MPR Building – North Side 93. Exterior – MPR Building – North Side
94. Exterior – MPR Building – North Side

Color	Substrate

Beige                        Stucco Beige                        Stucco Blue                          Metal Blue                          Metal
White	CT Beige                        Stucco Beige                        Stucco
Blue	Stucco Beige                         Metal Beige	Stucco
Blue                          Metal Blue                          Metal Beige                         Metal Blue                          Metal Blue                          Metal White                        Stucco Beige                        Stucco Blue                          Metal
Beige	Metal

Component

Wall Wall
Door Frame Door Wall Wall Sofit Facia
Window Frame Wall
Door Frame Door Drainpipe
Window Frame Door Sofit Wall
Window Frame

Drainpipe

Condition

I I I I I I I I I I I I I I I I I I
I

XRF Result (mg/cm2)

0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00 0.00
0.00

SURVEY FOR LEAD BASED PAINT Clovis Unified School District

Site Name:

Address:

Cole Elementary School

615 West Stuart Ave., Clovis, CA

Date:

FACS Job #:

1/10/24

PJ80246

Start Time:	1007

End Time:	1152

Calibration:

Calibration:

1.04 = 1.02

1.04 = 1.03

1.04 = 1.01

1.04 = 1.05

1.04 = 1.02

1.04 = 1.08

Technician:

Inspector/Assessor:

Sean Baker / Troy O’Connor

Chris Chipponeri

SciAps X-550Pb	Readings in red are lead-based.

Condition Codes:
I = Intact, F = Fair, P = Poor

No.	Sample Location

95. Exterior – Portico – East Side 96. Exterior – Portico – East Side 97. Exterior – Portico – East Side
98. Exterior – Portables 24-28 – South Side

99. Exterior – Portables 24-28 – South Side

Color	Substrate

Blue                          Metal White                        Stucco Blue                          Metal Blue                          Metal
Beige	Metal

Component

Support Pole Sofit
Support Pole Handrail
Drainpipe

Condition

I I I F
I

XRF Result (mg/cm2)

3.79 0.00 3.53 0.00
0.01

100 Exterior – Portables 24-28 – South Side 101 Exterior – Portables 24-28 – South Side 102 Exterior – Portables 24-28 – East Side 103 Exterior – Portables 29-35 – East Side 104 Exterior – Portables 29-35 – North Side 105 Exterior – Portables 29-35 – North Side 106 Exterior – Portables 29-35 – North Side 107 Exterior – Portable 30 – West Side
108 Exterior – Portable 30 – West Side 109 Exterior – Portable 30 – South Side 110 Exterior – Portable 30 – South Side 111 Exterior – Portable 30 – South Side 112 Exterior – Portable 31 – South Side
113 Exterior – Portable 31 – South Side

Beige                         Wood Beige                         Metal Beige                         Metal Beige                         Metal Beige                         Metal Beige                         Wood Blue                          Metal Blue                          Wood Beige                         Wood Blue                          Metal Blue                          Metal Blue                          Metal Beige                         Wood
Blue	Wood

Wall                      I                      0.00 Skirt                      I                      0.00 Support Beam              I                      0.00 Support Beam              I                      0.00 Skirt                      I                      0.00 Wall                      I                      0.00 Handrail                  F                      0.00
Window Frame             F                      0.00 Wall                      F                      0.00 Handrail                  F                      0.04 Door Frame                I                      0.00 Door                      I                      0.00
Wall	I	0.00

Window Frame	I	0.00

SURVEY FOR LEAD BASED PAINT Clovis Unified School District

Site Name:

Address:

Cole Elementary School

615 West Stuart Ave., Clovis, CA

Date:

FACS Job #:

1/10/24

PJ80246

Start Time:	1007

End Time:	1152

Calibration:

Calibration:

1.04 = 1.02

1.04 = 1.03

1.04 = 1.01

1.04 = 1.05

1.04 = 1.02

1.04 = 1.08

Technician:

Inspector/Assessor:

Sean Baker / Troy O’Connor

Chris Chipponeri

SciAps X-550Pb	Readings in red are lead-based.

Condition Codes:
I = Intact, F = Fair, P = Poor

No.	Sample Location	Color	Substrate	Component	Condition

XRF Result (mg/cm2)

114 Exterior – Portable 31 – South Side 115 Exterior – Portable 31 – East Side 116 Exterior – Portable 31 – South Side
117 Exterior – Covered Playground Seating – South Side 118 Exterior – Covered Playground Seating – North Side 119 Exterior – Pump House – North Side
120 Exterior – Pump House – North Side

121 Exterior – Pump House – West Side 122 Exterior – Pump House – West Side 123 Exterior – Pump House – North Side 124 Exterior – Pump House – North Side 125 Exterior – Pump House – South Side
126 Exterior – MPR Building – South Side

Beige                         Metal Beige                         Wood Blue                          Metal Black                         Metal Black                         Metal
Beige	Stucco Beige                         CMU

Beige	Metal White                        Stucco
Blue	Metal Blue	Metal Blue	Metal
Blue	Metal

Skirt                      I                      0.00 Wall                      I                      0.00 Flashing                   I                      0.00 Support Pole               I                      0.00 Support Beam              I                      0.00 Wall                      I                      0.01
Wall	I	0.00 Electrical
Pannel	I	0.00

Soffit                      I                      0.00 Door Frame                I                      0.00 Flashing                   I                      0.00 Plenum                    I                      0.00
Gait	I	0.00

CUSD Cole ES – Exterior Hazardous Materials Survey for Repainting	1/31/2024	Appendix C

Appendix C

Site Photos and Sample Location Drawing

		

Beige Paint on Stucco – Fair Condition
	
Stucco

Tan Paint on Metal Door Frame
	
Grey Paint on Metal Downspout

www.forensicanalytical.com	Forensic Analytical Consulting Services

Pb02	Pb04	Pb05	Pb11

Pb06

Pb07

Pb10 Pb09

Pb12

01C	Pb03	Pb01	Pb08	01A	01B

2440 West Shaw Suite #105 Fresno, CA 93711
	
N
	Sample Location

COLE ELEMENTARY SCHOOL EXTERIOR PAINT SURVEY
	
CLOVIS UNIFIED SCHOOL DISTRICT
	DRAWN BY: Sean Baker
	
				LOCATION:
615 W. STUART AVE. CLOVIS, CA
	FACS PROJECT No.: PJ80246
	
This is a design drawing and is the property of Forensic Analytical Consulting Services, Inc. It is not intended to replace required architectural or engineering plans.

CUSD Cole ES – Exterior Hazardous Materials Survey for Repainting	1/31/2024	Appendix D

Appendix D

Certifications of Personnel and Laboratories

www.forensicanalytical.com	Forensic Analytical Consulting Services

Forensic Analytical Consulting Services, Inc.

This is to confirm that

Sean-Paul Baker Has attended the four-hour

AHERA Refresher Course for Asbestos Inspectors And has completed the requisite training for asbestos accreditation under TSCA Title II September 05, 2023

CertificateNumber:FACSBIR1513

Valid Until: 9/05/24

Cal/OSHA Approval Number: CA-025-06

Fred J. Vinciguerra, Chief Executive Officer Forensic Analytical Consulting Services,Inc. 21228 Cabot Blvd, Hayward, CA 94545 (800) 677-1483

Parra Environmental Training

This is to confirm that

Troy O'conner Has attended the Twenty- four-hour

AHERA Initial Course for Asbestos Inspectors

And has completed the requisite training and passed the exam for asbestos accreditation under TSCA Title II for the purposes of certification required by Title 8, Article 2.7, Chapter 3.2, Section 341.16 approved by CAL-DOSH
Course Date: 11-13-2023 to 11-15-2023

Certificate Number: PETBII1000005 Valid Until: November 15, 2024 Cal/OSHA Approval Number: CA-025-05

Hermes Parra
Parra Environmental Training 3498 Clayton Rd. Suite 201 Concord CA 94519 (925) 270-3040

http://www.parraenviro.com

*This document contains a Watermark If the diagonal PET in gray is not present, this document is not valid.

Forensic Analytical Consulting Services, Inc.

This is to confirm that

Chris Chipponeri Has attended the four-hour

AHERA Refresher Course for Asbestos Inspectors And has completed the requisite training for asbestos accreditation under TSCA Title II September 05, 2023

CertificateNumber:FACSBIR1518

Valid Until: 9/05/24

Cal/OSHA Approval Number: CA-025-06

Fred J. Vinciguerra, Chief Executive Officer Forensic Analytical Consulting Services,Inc. 21228 Cabot Blvd, Hayward, CA 94545 (800) 677-1483

STATE OF CALIFORNIA DEPARTMENT OF PUBLIC HEALTH

LEAD-RELATED CONSTRUCTION CERTIFICATE

INDIVIDUAL:	CERTIFICATE TYPE:	NUMBER:	EXPIRATION DATE:

Lead Inspector/Assessor	LRC-00000782	6/20/2024

Chris Chipponeri

Disclaimer: This document alone should not be relied upon to confirm certification status. Compare the individual’s photo and name to another valid form of government issued photo identification. Verify the individual’s certification status by searching for Lead-Related Construction Professionals at www.cdph.ca.gov/programs/clppb or calling (800) 597-LEAD

United States Department of Commerce National Institute of Standards and Technology

Certificate of Accreditation to ISO/IEC 17025:2017

NVLAP LAB CODE: 101459-0

SGS Forensic Laboratories Hayward, CA

is accredited by the National Voluntary Laboratory Accreditation Program for specific services, listed on the Scope of Accreditation, for:

Asbestos Fiber Analysis

This laboratory is accredited in accordance with the recognized International Standard ISO/IEC 17025:2017. This accreditation demonstrates technical competence for a defined scope and the operation of a laboratory quality
management system (refer to joint ISO-ILAC-IAF Communique dated January 2009).

2023-07-01 through 2024-06-30

Effective Dates	For the National Voluntary Laboratory Accreditation Program

National Voluntary

Laboratory Accreditation Program

SCOPE OF ACCREDITATION TO ISO/IEC 17025:2017

SGS Forensic Laboratories 3777 Depot Road, Suite 409 Hayward, CA 94545-2761 Nerissa Platon Phone: 510-266-8183
Email: nerissa.platon@sgs.com http://www.falaboratories.com

ASBESTOS FIBER ANALYSIS	NVLAP LAB CODE 101459-0

Bulk Asbestos Analysis

Code	Description

18/A01	EPA -- 40 CFR Appendix E to Subpart E of Part 763, Interim Method of the Determination of Asbestos in Bulk Insulation Samples

18/A03	EPA 600/R-93/116: Method for the Determination of Asbestos in Bulk Building Materials

Airborne Asbestos Analysis

Code	Description

18/A02	U.S. EPA's "Interim Transmission Electron Microscopy Analytical Methods-Mandatory and Nonmandatory-and Mandatory Section to Determine Completion of Response Actions" as found in 40 CFR, Part 763, Subpart E, Appendix A.

For the National Voluntary Laboratory Accreditation Program

Effective 2023-07-01 through 2024-06-30	Page 1 of 1

AIHA Laboratory Accreditation Programs, LLC acknowledges that

SGS Forensic Laboratories

3777 Depot Rd, Suite 409, Hayward, CA 94545-2761 Laboratory ID: LAP-101762

along with all premises from which key activities are performed, as listed above, has fulfilled the requirements of the AIHA Laboratory Accreditation Programs, LLC (AIHA LAP) accreditation to the ISO/IEC 17025:2017 international standard, General Requirements for the Competence of Testing and Calibration Laboratories in the following:

LABORATORY ACCREDITATION PROGRAMS

INDUSTRIAL HYGIENE

ENVIRONMENTAL LEAD

ENVIRONMENTAL MICROBIOLOGY

FOOD

UNIQUE SCOPES

BERYLLIUM FIELD/MOBILE

Accreditation Expires: July 01, 2025

Accreditation Expires: July 01, 2025

Accreditation Expires: July 01, 2025

Accreditation Expires:

Accreditation Expires:

Accreditation Expires:

Specific Field(s) of Testing/Method(s) within each Accreditation Program for which the above named laboratory maintains accreditation is outlined on the attached Scope of Accreditation. Continued accreditation is contingent upon successful on-going compliance with ISO/IEC 17025:2017
and AIHA LAP requirements. This certificate is not valid without the attached Scope of Accreditation. Please review the AIHA LAP website (www.aihaaccreditedlabs.org) for the most current Scope.

_____________________________________

Cheryl O Morton

Managing Director, AIHA Laboratory Accreditation Programs, LLC

Revision21: 05/15/2023	Date Issued: 08/01/2023

Right People

Right Perspective

Right Now

www.forensicanalytical.com