ADDENDUM NO. 3	DATE: 03/29/23

PROJECT:

McKinley/ Fowler Elementary School- Increment2- Electrical Rebid Fresno, CA
CUSD Bid No.: 2932

OWNER:

Clovis Unified School District 1450 E. Herndon Ave.
Clovis, CA 93611

ARCHITECT:

DARDEN ARCHITECTS, INC.

Attention: Andrew Corral/ Mike Fennacy 6790 N. West Avenue
Fresno, California 93711 T.	(559) 448-8051
F.	(559) 446-1765

DARDEN PROJECT NO. 2116 DSA File Nos. 10-48
DSA APPL. NO. 02-120543

It will be the responsibility of the General Contractor to submit the information contained in this addendum to all its subcontractors and suppliers. Acknowledge receipt of this Addendum in the space provided on the Bid Form. Failure to do so may subject Bidder to disqualification.

The following additions, deletions, and revisions to the SHEETS and Project Manual are hereby made and do become a part of these Contract Documents.

PROJECT: McKinley/ Fowler Elementary School- Increment 2

ADDENDUM NO. 3	...........................................................................................................DATE: 03/29/23 PAGE 2

INDEX OF ADDENDATRANSMITTED HEREWITH PROJECT MANUAL:

CHANGES TO CONDITIONS OF THE CONTRACT................................................................. AD3-CCC01

SPECIFICATIONS:

CHANGES TO SPECIFICATIONS............................................................................AD3-SP01 THRU SP02

SHEETS:

CHANGES TO SHEETS:

ELECTRICAL........................................................................................................................AD3-E01 THRU AD3-E04

ATTACHMENTS:

SHEETS:

ELECTRICAL .....................................................................................................................AD3-EX01 thru AD3-EX04.

PROJECT MANUAL:

BIDDING AND CONTRACT REQUIREMENTS:

CHANGES TO CONDITIONS OF THE CONTRACT:

AD3-CCC01	 Refer to the attached Owner Controlled Insurance Program (OCIP) criteria as indicated with the AD3 in the upper-right-hand corner.

SPECIFICATIONS:

CHANGES TO SPECIFICATIONS:

AD3-SP01	Refer to Specification Section01 11 13- SUMMARY OF WORK:

1. Add the attached BID SCHEDULE document to the end of this section as identified with an AD-1 in the upper right-hand corner.

PROJECT: McKinley/ Fowler Elementary School- Increment 2- Electrical Rebid

ADDENDUM NO. 3..............................................................................................................DATE: 03/29/23 PAGE 3

SHEETS:

CHANGES TO SHEETS:

ELECTRICAL:

AD3-E01	 Refer to SheetX/E501 – FIRE ALARM SYSTEM- SYMBOL, SITE PLAN, NOTES, AND DETAILS:
1. Remove and Replace X/E501 – FIRE ALARM SYSTEM- SYMBOL, SITE PLAN, NOTES, AND DETAILS with the attached Sheet AD3-EX01.
AD3-E02	Refer to SheetX/E502 – FIRE ALARM SYSTEM- SINGLE LINE DIAGRAM:

1. Remove and Replace X/E501 – FIRE ALARM SYSTEM- SINGLE LINE DIAGRAM with the attached Sheet AD3-EX02.

AD3-E03	Refer to SheetA/E201-BUILDING A- POWERPLAN:

1. Remove and Replace A/E201- BUILDING A- POWER PLAN with the attached Sheet AD3-EX03.

AD3-E04	Refer to SheetA/E401-BUILDING A- LOW VOLTAGE PLAN:

1. Remove and Replace A/E401- BUILDING A- LOW VOLTAGE PLAN with the attached Sheet AD3-EX04.

END OF ADDENDUM NO. 3

AD-3

Clovis Unified School District, LLC

Owner Controlled Insurance Program (OCIP)

Project: Fowler McKinley Elementary School Project #: Clovis-02
IMPORTANT: When enrolling online insert project number above as project code!!

PRESENTED BY:

Gallagher Construction Services

2023 Arthur J. Gallagher & Co.

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# Clovis-02	AD-3

Table of Contents

Sections	Page

An Introduction to the OCIP Program........................................................................................................1

Insurance Coverages.................................................................................................................................3

Program Eligibility......................................................................................................................................5

Enrollment Responsibilities Flow Chart......................................................................................................6

Insurance Required From Contractors of Any Tier ....................................................................................7

Online Enrollment Instructions - AJG/VUE Online Portal...........................................................................8

Accident Reporting for General Liability Claims.......................................................................................20

Definitions for Purposes of This Manual ..................................................................................................21

Personnel Directory .................................................................................................................................22

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

An Introduction to the OCIP Program

This manual outlines the details and instructions for all parties for this Owner Controlled Insurance Program (“OCIP”). Clovis Unified School District (“Owner”) provides Commercial General Liability, and Umbrella Liability coverage for the Construction Manager Bush Construction (“CM”), and all enrolled subcontractors of any tier while working on the Fowler McKinley Elementary School project.

Major benefits
•	Uniformity of coverage terms and conditions •	Reduced Administrative burden
•	Insurance costs will not increase for subcontractors during the project •	Reduces coverage disputes, litigation and subrogation
•	Immediate Insurer response for subcontractors’ accidents •	One Insurer for all completed operations claims
•	Project Specific Limits of Liability

Coverage provided
General Liability and Umbrella Liabilty Insurance

The OCIP program provides $100,000,000 of liability limits during construction, and a separate $100,000,000 completed operations limit during for the State Statute of Repose or Ten (10) years following substantial completion, whichever is less. Limits apply to the Owner, Construction Manager and all subcontractors with one $100,000,000 general aggregate and a $100,000,000 limit for products/completed operations.

Subcontractor Enrollment
All subcontractors and lower tier subcontractors MUST enroll online through the Gallagher Contractor Portal http://ajg.vuewrapup.com/contractorportal. Each subcontractor will receive a Certificate of Insurance listing them as a Named Insured and specifying the job name and Owner project number. This program is mandatory for all subcontractors of any tier. However, it will not be extended to environmental subcontractors, subcontractors working under a Professional Services Agreement (PSA), Construction Staking and Surveying Agreement, or other similar professional services only agreement.
Failure to comply with enrollment requirement may result in a 2% charge against your contract value until compliant.

Subcontractor Bid Deduction
Subcontractors will exclude in their bids their normal costs of insurance for general liability and excess liability. Change Orders are also to be processed without the cost of the same insurance coverages.

Project Term

February 14, 2023 to February 1, 2027

Insurance Carriers:
General Liability: Everest Indemnity Insurance Company 1st Excess Liability: Everest Indemnity Insurance Company
2nd Excess Liability: Crum & Forster Specialty Insurance Company
3rd Excess Liability: Arch Specialty Insurance Company (Quota Share) 3rd Excess Liability: Ascot Specialty Insurance Company (Quota Share)

PAGE 1

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

4th Excess Liability: Great American Assurance Company (Quota Share) 6th Excess Liability: Scottsdale Insurance Company (Quota Share)

Deductible Charge for Losses
Subcontractors shall be responsible for the first $5,000 of any General Liability losses within the deductible amount for such insurance to the extent such loss results from the fault or neglect of a subcontractor of any tier, or someone for whom either may be responsible.

Subcontractor Off-site Coverage
Owner will still require Certificates of Insurance for Workers’ Compensation, Automobile, and off-site General Liability and Excess Liability and Professional Liability where applicable coverages as required by subcontract.

Subcontractor Excess Limits
Each insured subcontractor should discuss this program with its own insurance advisor to see if additional coverages are recommended. Any such additional coverage will be at the subcontractors’ own expense. Should Owner purchase additional limits of liability for any specific project, those will be disclosed.

Claims Management
Claims will be reported to Owner, Construction Manager and Gallagher Construction Services as required by this Manual. Gallagher Construction Services maintains full service claims departments experienced in handling construction related claims. Our claim professionals will assist you with any claims related questions.

DISCLAIMER - This is a summary of the OCIP Program only. It does not change, alter or modify the policy terms and conditions in any way. Actual policy forms and Endorsements are available upon request.

PAGE 2

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

Insurance Coverages

The Owner provides the following Owner Controlled Insurance Program (“OCIP”) to all enrolled subcontractors under the program. Policy copies are available upon request.

a. Commercial General Liability Insurance

(Excluding Workers’ Compensation, Automobile, and Professional) applying to all Insureds jointly with the following Bodily Injury and Property Damage combined limits:

Limits
		
$2,000,000
	Each Occurrence
	
$2,000,000
	Personal and Advertising Liability
	
$4,000,000
	General Aggregate
	
$4,000,000
	Products and Completed Operations Aggregate
	
Excluded
	Damages to Premises Rented to You
	
Excluded
	Medical Expense

Completed Operations coverage is provided for the statute of repose or ten (10) years, whichever is less.

b. Excess Liability Insurance

Limits
		
$100,000,000
	Each Occurrence
	
$100,000,000
	General Aggregate
	
$100,000,000
	Products and Completed Operations Aggregate

a. General Liability Deductibles: For each contractor per occurrence

Subcontractors shall be responsible for the first $5,000 of any General Liability or Contractors Pollution Liability losses within the deductible amount for such insurance to the extent such loss results from the fault or neglect of the Contractor, a subcontractor of any tier, or someone for whom either may be responsible. It is your responsibility to familiarize yourself with the requirements and responsibilities associated with losses and the assessment of deductibles associated with losses under this program.

b. Defense Costs
Defense costs are in addition to the limits of liability of the OCIP Policies.

The coverages under this program do not include all insurance needed by the Subcontractor and its Subcontractors of any tier. For example, General Liability, Excess coverages apply only to the operations of and for each Insured at the Project Site. They do not apply to the operations of any Insured in their regularly established main or branch office, factory, warehouse, or similar place.

PAGE 3

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

This summary is not intended to amend or alter any provisions of the actual insurance policies. If a conflict should occur, the insurance policies shall govern. Actual policy copies will be provided upon written request.

PAGE 4

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

Program Eligibility

All qualified subcontractors of any tier whose employees perform actual on-site labor are required to participate in the Owner’s OCIP and follow through with the enrollment and participant responsibilities as noted throughout this Manual.

Coverage Trigger
Coverage will begin the date you begin work at the site and is contingent on completing the OCIP Enrollment Online through the Gallagher Contractor Portal at http://ajg.veuwrapup.com/contractorportal. Once your enrollment has been completed you will receive a Certificate of Insurance confirming the coverage from Gallagher Construction Services. It is your responsibility to complete and satisfy all enrollment requirements before you begin work on the project. Failure to supply all requested insurance documents, will result in a flat 2% charge against your entire contract amount. You are also responsible for ensuring that any lower tier subcontractors you hire complete the Online Enrollment before they begin their work at the project site. If you or your lower tier subcontractors have NOT completed the Online Enrollment process and have NOT received confirmation of enrollment from Gallagher Construction Services, no coverages will be afforded, and you will not be permitted onsite.

Ineligible Parties
Subcontractors who present an exceptionally hazardous exposure or risk to the job site may not be eligible to participate, at Owner’s discretion. It is your responsibility to contact Gallagher and confirm your eligibility before you begin work on the project.

Not everyone will be a participant. For example, the following are ineligible for the program: Subcontractors of any tier that are:

•      Architects •      Engineers
•	Consultants •	Vendors
•	Suppliers
•	Material dealers,
•	Off-site fabricators with no on-site installation
•	Others who merely transport, pick up, deliver or carry materials, personnel, parts or equipment or any other items or persons to or from the project site
•	Hazardous material / abatement, or asbestos abatement contractors

If you are uncertain whether your firm will be a participant in this program, or wish confirmation of your eligibility, please contact the administrator at Gallagher Construction Services. Contact information can be found on the personnel page at the end of the manual.

Construction Manager will coordinate the program at the project site. Gallagher Construction Services will be administering the program from their offices. A complete contact list is in the back of this Manual.

PAGE 5

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

Enrollment Responsibilities Flow Chart

#
	Action Item
	Responsibility

1
	Distribute Manual to prospective bidders or subcontractors.
	
Construction Manager

2
	Send Manual to your Insurance Agent/Broker for assistance, if necessary, in completing the Online Enrollment.
	
Subcontractor

3
	Distribute Manual to prospective lower tier bidders/subcontractors.
	
Subcontractor

4
	Complete Online Enrollment and forward to Gallagher insurance documents from you and your lower tier subcontractors.
	
Subcontractor

5
	Upload off-site Insurance Certificate to Gallagher Contractor Portal in accordance with the Insurance Requirements of the Subcontract Agreement

Subcontractor

6
	Confirm all site subcontractors’ and/or lower-tier subcontractor(s) enrollment in program. Gallagher will issue written confirmation.

Gallagher

7
	Certificate of Insurance, Insurance Cost Worksheet and policy copies upon request.
	
Gallagher

8
	Advise your Insurance Agent/Broker of insurance coverages provided by Construction Manager so that proper notice can be made to your current insurers.
	
Subcontractor Lower-tier subcontractor

PAGE 6

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

Insurance Required From Contractors of Any Tier

Please note that the coverages provided by Clovis Unified School District are designated to cover you only while you are actively engaged in construction activities at the project site. Therefore, it is imperative that you maintain your own insurance coverage for off-site operations.

The required insurance of every participant is outlined in detail below. You are required to upload your certificate of insurance to the Gallagher Contractor Portal which shows the following offsite coverages along with the minimum limits as follows:

1.	 Statutory Workers' Compensation Insurance and $1,000,000 Employers’ Liability for on & off-site operations, warranty and call-back work.

2.	 General Liability Insurance for off-site operations. The required limits vary depending on the type of work performed by the subcontractor. However, required limits are not less than $1,000,000 per occurrence and $2,000,000 for Products and Completed Operations and General Aggregate.

3.	 Excess/Umbrella Liability Insurance for off-site operations. The required limits vary depending on the type of work performed by the subcontractor. However, required limits are not less than $1,000,000 per occurrence and General Aggregate

4.	Automobile Liability Insurance with limits not less than $1,000,000 combined single limit covering all owned, non-owned and hired automobiles.

5.	Professional Liability Insurance with limits not less than $2,000,000 per claim for all subcontractors, consultants, architects, engineers, or surveyors rendering professional services for the Fowler McKinley Elementary School project.

6.	The Subcontractor of any tier shall require their respective vendors, suppliers, off-site fabricators, material dealers, truckers, drivers and others who merely transport, pick-up, deliver or carry materials, personnel, parts or equipment to or from the project site to maintain insurance in the form and with the limits as specified in this Insurance Manual.

The Insurance Manual outlines in detail the required coverages for all participants. It is important to review this document and supply the required Certificate of Insurance prior to the start of work. Please note that progress payments may be withheld if required insurance is not on file. If you have questions regarding any of the required insurance, feel free to contact the administrator at Gallagher Construction Services. Contact information can be found on the personnel page at the end of the manual.

PAGE 7

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

Online Enrollment Instructions – AJG/VUE Online Portal

To start please open your internet browser and go to the AJG Wrap-up Management Portal URL (https://ajg.vuewrapup.com/contractorportal). This will open the portal login screen.

First time users please click here to register.

Step1: Registering and Logging In

Click the Register Me link at the bottom right hand corner of the login box. If you are already registered, proceed to Step C.

A. Fill in the form with your first name, last name, email ID (email address) and enter the user ID you would like to use. Your user ID can be any name or phase you will easily remember, such as your first initial and last name (preferred), your company name, or your email address. Password must contain letters, numbers and symbols.

a. All fields in yellow are required

b. FEIN (your company’s Federal Tax Identification Number) field is optional, but recommended as it will link your account to any existing contracts linked to your company

PAGE 8

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

B. When your registration has been completed successfully, you will see the message “User ID and Password are created”. Please click here to login to “Contractor Portal”. Click the link to be redirected to the login page where you can login to the portal to complete your enrollment. You will also receive an email with your User ID and Password for your records.

C. Use your provided or created User ID and Password to login. If any error messages appear, contact your AJG Wrap-up Administrator.

Step 2: Completing an Enrollment

A. If your incomplete enrollment already has a contract in the system, you may be required to fill in the missing details. Your contract can be selected by clicking on the contract number hyperlink in the Contract # column.

B. If you do not see a contract for the specific project you are enrolling in, click the “New Enrollment” button.

PAGE 9

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

C. When the user clicks on the New Enrollment link, a pop up screen will open as shown below. Users should provide the Project Code as listed in their Wrap Up manual or provided by their Wrap Up Administrator.

Step 3: Enrolling

A. The Enrollment Screen includes the following sections, each of which can be expanded or collapsed for ease of review:

a. Provide Company Information b. Provide Contract Information c. Provide Contact Information d. Provide Address Information
e. Provide Estimated Payroll for work performed on the Contract f.	Provide Additional Information
g. Approval and Signature

PAGE 10

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

B. Fill in each section with your information to the best of your ability. Every section is required to be completed.

a. For a new enrollment, all fields should be filled in

1. If your company has previously enrolled in a contract on our portal, you will have an option to select previous information in some fields

b. If a contract has been added to your portal by an AJG Wrap-up Administrator, you may not be able to edit some fields. Move on from those and fill in all the other fields as completely as possible

c. If you notice a mistake in a non-editable field, contact your AJG Wrap-up Administrator

d. If you are not sure what a field is requesting, hovering over the field title will show captioned explanations

PAGE 11

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

C. In the Contact section you must enter at least one contact and it must be marked as primary. You may also add additional contacts i.e. Payroll Contact or Worker’s Comp Claim Con.

a. You must provide a value for your corresponding preferred mode of contact. For example, if you select email as your preferred method of contact, you must provide an email address.

b. If the enrolling contractor has existing contacts available in our system, they can make a selection from the existing records by selecting contact information from the dropdown available on top of each contact box. Once selected, the contact details will be populated in the respective fields.

c. User can manually enter the new contact by performing these steps: Select contact type, from dropdown menu; enter First Name, Last Name, Email, Phone, and Mobile. By default, the Primary checkbox will be marked for the first contact added. Please note, that the email is mandatory.

d. To add an additional contact, click the ADD

e. Once a second Contact is added the CLEAR

button

and DELETE	button will be available for existing

Contact block, allowing the user to clear the details and re-enter or delete the record if needed

PAGE 12

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

A. In the Address section, enter a primary address by filling in all fields and checking the checkbox “Primary”. You must enter at least one address, and if there is only one it must be marked as primary.

a. To add a secondary address, click the ADD	button in the lower left hand corner of the section containing that address

b. Once another address is added, the CLEAR            and DELETE            button will be displayed for the existing Address block, allowing the user to clear the details and re-enter or delete the record if needed

c. Note: You cannot delete an address that has already been approved by the AJG Wrap-up Administrator. If there is an error in the address approved or entered by the AJG Wrap-up Administrator, please contact them directly.

B. In the Estimated Payroll section, you must enter your best estimate of payroll for entirety of the project.

a. You must submit estimated payroll for all General Liability Class Codes you will be working under on the project. To add estimated payroll for additional codes, please press the Add	button on the lower right hand corner of the section.

C. Before you submit your enrollment information, you must check the confirmation checkbox. (Note: The text in your portal may differ from what is shown in the screenshot.) Once you have verified that all information entered is correct, please check the checkbox, and type your name in the Signature box.

PAGE 13

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

D. If you do not have all the necessary information needed for your enrollment, you are now allowed to save the information that you have input and come back to finish at a later time.

After pressing the Save for Later or Submit button be sure to confirm your selection before leaving the page. If you do not, your enrollment will not be saved or submitted in any way.

E. Once your Contract is submitted, you cannot make changes to the enrollment.

Step 4: Uploading Documentation

A. As part of your enrollment, you may be required to submit supporting documentation such as:

a. Insurance Policy Rate and Declaration Pages b. Certificates of Insurance
c. NKLL (No Known Loss Letters) d. Other Documents

The system will prompt you as to which documents are required.

PAGE 14

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

B. Accessing the Documents screen

a. Once you have submitted your enrollment you can press the Documents button on the top Right

On the Documents screen you must choose from the Select Document Category and Select File to upload the document. Refer to the image below. If there are existing document(s) for the selected Contract, the system will display those under Documents section.

1

2

3

C. To add the documents to the selected Contract, follow the steps below:

a. Select the Document Category from the available options. Note: A user can select multiple Categories, i.e. “GL Dec and Rate Pages” and “Excess Rate and Dec Pages”

b. To locate the file to upload, browse your local drive by clicking on the Browse button. The file must be available on your device or computer from which you are currently accessing the portal.

c. Once the file is successfully uploaded, the document(s) will be listed in the Documents section of the Documents Screen

Notes:	Only PDF, DOC, DOCX or TIFF documents can be uploaded and all files must be 10MB or under.

PAGE 15

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

Step 5: Adding a Subcontract

If you need to add a Lower Tier Subcontractor please follow the below instructions.

A. From the Enrollment Screen select the Subcontract button on the top right hand corner.

B. This will bring you to the Sub Contract Screen. Begin by pressing the Add Subcontract button.

A. This will open a Subcontract enrollment Screen

a. Please fill out all information to the best of your ability

b. Business Name, FEIN # (If known),Subcontract Value, Expected Start Date

c. Contract # is a read only field

d. Verify the information and check the checkbox next to the statement “Statements in this application are true and accurate to the best of my knowledge”

e. Press Submit and confirm

PAGE 16

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

B. To add an additional subcontracts; click on the Add Sub Contract button again the first Sub Contract screen.

G. If you are entering Final Payroll, please check box next to “Is Final Payroll for contract?”

H. After all required information has been entered, click the Submit button. Please note: Once the payroll information has been submitted it is still editable and can be resubmitted as needed. If you are unable to edit please contact the AJG Wrap-up AJG Wrap-up Administrator for changes.

To print, click Print button on the top right corner of Actual Payroll screen. A PDF file will open displaying the details of the submitted Actual Payroll.

Step 6: Close Out

A. Once logged in to the portal site select the Contract # listed on the Home Screen, then Click on the Close Out button.

a. Note: If any of your Contract #’s are not listed, please contact your AJG Wrap-up AJG Wrap-up Administrator to check the status of enrollment

PAGE 17

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

B. Please fill out all fields

a. Notice of Completion Date: the day your company finished work on site

b. Completion Signature: The name of whomever is completing the form

c. Final Contract Value: Your final contract value with you Prime Contractor

d. Payroll Information: The final payroll amount for all Class Codes from your enrollment, for the entire project. Once all information is completed, please press the Submit button. You will see the message “Data Saved Successfully”.

e. Subcontractor Details: (if you did not hire any subcontractors please move to step 2) Any contractors you have hired that have already enrolled in our program will appear in the Existing Subcontracts Chart

PAGE 18

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

1. Your subcontractors’ reported final Contract Value will populate in the	column. column. To confirm or correct the Final Contract Value, you must fill in the
column.

2. If you did not hire any subcontractors select No, and press

If you did hire subcontractors and they are listed above select No, and press

If you did hire subcontractors and they are NOT listed above select Yes and add subcontracts in the Add Subcontracts chart by pressing the	button and filling in requested details.

3. Once all hired subcontracts are reported, please review your Close out and press

PAGE 19

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

Accident Reporting for General Liability Claims

If an injury is involved, the Subcontractor's superintendent must immediately arrange for first aid or other required medical treatment for the injured party.

All Incidents, regardless of severity, shall be reported immediately to the Job Site Contact and On-site Safety Coordinator and reported to the Insurer by telephone.

The Subcontractor's superintendent must complete a General Liability Loss Notice for each accident with the following distribution:

Karen Durley Gallagher
Direct: (949) 349-9632 karen_durely@ajg.com

Denver Stairs
Clovis Unified School District Direct: (559) 327-9260 denverstairs@cusd.com

Jasmine Cooper Bush Construction
Direct: (559) 267-6010 jasmine@bushconstruction.net

Any Court Summons, legal documents or other correspondence must be immediately referred to Gallagher Construction Services by registered mail. Additional questions concerning suit papers should be referred to Gallagher Construction Services.

PAGE 20

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

Definitions for Purposes of This Manual

Owner
	Clovis Unified School District
	
Construction Manager
	
Bush Construction

Project
	Fowler McKinley Elementary School
Between N. Highland Ave. & Leonard Ave. between Princeton Ave. & Weldon Ave.

Project Site
	The areas designated in writing by Construction Manager in a contract document for performance of the Work and such additional areas as may be designated in writing by Construction Manager for Contractor’s use in performance of the Work. The Project Site shall also include (1) field offices, (2) property used for bonded storage of material for the Project approved by Construction Manager, (3) staging areas dedicated to the Project. Items 1 through 3 must be approved by the OCIP Insurer and listed in the OCIP Policy

Off-Site Exposures
	
Offices, shops, warehouses, factories, or similar locations away from the designated project site that have not been approved by the OCIP Insurer and listed on the OCIP Policy ARE NOT COVERED.

Contract

The agreement between Construction Manager and the Subcontractor. The terms "Contract" and "Agreement" are used interchangeably.

Subcontractor of Any Tier
	
The person, firm or corporation with whom Construction Manager has entered into Agreement to perform the Work; or the Person or entity who has a contract with Construction Manager Subcontractor to perform any of the Work at the Site.

Work

Operations, as fully described in the Contract, performed at or emanating directly from the Fowler McKinley Elementary School project.

Insured
	Subcontractors of any tier which have an executed subcontract agreement and which have received written confirmation of coverage by Gallagher Construction Services.
The following are not Insureds under this WRAP-UP - Architects, engineers, consultants, vendors, suppliers, material dealers, off-site fabricators and others who merely transport, pick up, deliver or carry materials, personnel, parts or equipment or any other items or persons to or from the Project Site, et al.

PAGE 21

CLOVIS UNIFIED SCHOOL DISTRICT |FOWLER MCKINLEY ELEMENTARY SCHOOL |PROJECT NUMBER# CLOVIS-02	AD-3

Personnel Directory

Clovis Unified School District (Owner) Contacts	Bush Construction (CM) Contacts

Associate Superintendent, Administrative Services
	Michael Johnston
Clovis Unified School District
Direct: (559) 327-9110 michaeljohnston@cusd.com
	Project Administrator
	Veronica Gutierrez Bush Construction Direct: (559) 584-1575
vgutierrez@bushconstruction.net
	
Assistant Superintendent, Facility Services
	Denver Stairs
Clovis Unified School District
Direct: (559) 327-9260 denverstairs@cusd.com
	Project Manager
	Jasmine Cooper Bush Construction Direct: (559) 267-6010
jasmine@bushconstruction.net
	
		Safety Coordinator
	Brockton Wheeler Bush Construction Direct: (559) 670-2449
bwheeler@bushconstruction.net

Gallagher (Insurance Broker) Contacts

*Enrollment/ Administration
	Ariana Daniels Gallagher
Direct: (725) 735-3907 ariana_daniels@ajg.com
	Program Director
	Anthony Carlton Gallagher
Direct: (619) 651-5317 anthony_carlton@ajg.com
	
Program Manager
	Richard E. Banlowe Gallagher
Direct:: 818-539-1210 Mobile: 805-630-4339 richard_banlowe@ajg.com
	Client Service Supervisor
	Peggy L. Wylie Gallagher
Direct: (925) 953-5266 peggy_wylie@ajg.com
	
		General Liability Claims
	Karen Durley Gallagher
Direct: (949) 349-9632 karen_durely@ajg.com

PAGE 22

AD-3

	Mode	
days?
18
2/1	2/1
Rebid AD-3

CLOVIS UNIFIED	NEW CLOVIS ELEMENTARY FOWLER / McKINLEY	BUSH / DARDEN

ID	Task	Task Name	Duration	Start	Finish	Predecessors	Qtr 4, 2022 Oct	Nov
days?
1	McKINLEY - FOWLER ELEMENTARY	450	Mon 11/28/22 Fri 8/16/24 2                                       INCREMENT 1 PRE-BID OVERVIEW	217	Mon 11/28/22 Tue 9/26/23

3	BIDDER PREQUALIFICATION PACKAGE DUE	14 days Mon 11/28/22 Thu 12/15/22

Qtr 1, 2023	Qtr 2, 2023	Qtr 3, 2023 Dec	Jan	Feb       Mar        Apr	May        Jun         Jul	Aug

BIDDER PREQUALIFICATION PACKAGE DUE

Qtr 4, 2023 Sep	Oct	Nov

Qtr 1, 2024 Dec	Jan	Feb

Qtr 2, 2024 Mar	Apr	May

Qtr 3, 2024
Jun	Jul	Aug	Sep

4	BIDDER PREQUALIFICATION PACKAGE DUE	4 days 5	FIRST ADVERTISEMENT	5 days 6	SECOND ADVERTISEMENT	5 days 7	1st PRE-BID JOBSITE MEETING W/ PRIMES	1 day 8	2nd PRE-BID JOBSITE MEETING W/ PRIMES	1 day 9	PROJECT BID DATE	1 day
10	CUSD REVIEW BID PACKAGES	5 days 11	BOARD AGENDA INFORMATION	4 days 12	BOARD APPROVAL	1 day 13	DSA APPROVED PLANS	1 day 14	ISSUE PRIME-CONTRACTS	10 days 15	CUSD LETTER OF INTENT	1 day
16	INCREMENT 1 CONSTRUCTION PHASE OVERVIEW 217 days?

17	MOBILIZE	20 days 18	EATHWORK	20 days 19	UNDERGROUND UTILITIES	25 days 20	BALL FIELDS	25 days
21	SITE CONCRETE	25 days

Mon 12/12/22

Tue 1/3/23

Mon 1/9/23

Tue 1/10/23

Wed 1/11/23

Wed 2/1/23

Thu 2/2/23

Thu 2/9/23

Wed 2/15/23

Wed 2/15/23

Thu 2/16/23

Thu 2/16/23

Mon 11/28/22

Thu 2/16/23

Thu 2/23/23

Thu 3/23/23

Thu 3/23/23

Thu 4/27/23

Thu 12/15/22

Mon 1/9/23

Fri 1/13/23

Tue 1/10/23

Wed 1/11/23

Wed 2/1/23

Wed 2/8/23

Tue 2/14/23

Wed 2/15/23

Wed 2/15/23

Wed 3/1/23

Thu 2/16/23

Tue 9/26/23

Wed 3/15/23

Wed 3/22/23

Wed 4/26/23

Wed 4/26/23

Wed 5/31/23

3SS+10 days

5SS+4 days

6SS+1 day

7

9

11

11

12

12

12

14SS+5 days

18

19

BIDDER PREQUALIFICATION PACKAGE DUE

FIRST ADVERTISEMENT

SECOND ADVERTISEMENT

1st PRE-BID JOBSITE MEETING W/ PRIMES

2nd PRE-BID JOBSITE MEETING W/ PRIMES PROJECT BID DATE

CUSD REVIEW BID PACKAGES

BOARD AGENDA INFORMATION

BOARD APPROVAL

DSA APPROVED PLANS

ISSUE PRIME-CONTRACTS

CUSD LETTER OF INTENT

MOBILIZE

EATHWORK

UNDERGROUND UTILITIES

BALL FIELDS

SITE CONCRETE

Page 1

	Mode	
days?
27
3/2	3/2
3/17	4/13
Rebid AD-3

CLOVIS UNIFIED	NEW CLOVIS ELEMENTARY FOWLER / McKINLEY	BUSH / DARDEN

ID	Task	Task Name	Duration	Start	Finish	Predecessors	Qtr 4, 2022 Oct	Nov
22	INCREMENT 2 PRE-BID OVERVIEW	217	Mon 11/28/22 Tue 9/26/23

23	BIDDER PREQUALIFICATION PACKAGE DUE	14 days Mon 11/28/22 Thu 12/15/22

Qtr 1, 2023	Qtr 2, 2023	Qtr 3, 2023 Dec	Jan	Feb       Mar        Apr	May        Jun         Jul	Aug

BIDDER PREQUALIFICATION PACKAGE DUE

Qtr 4, 2023 Sep	Oct	Nov

Qtr 1, 2024 Dec	Jan	Feb

Qtr 2, 2024 Mar	Apr	May

Qtr 3, 2024
Jun	Jul	Aug	Sep

24	BIDDER PREQUALIFICATION PACKAGE DUE 25	FIRST ADVERTISEMENT
26	SECOND ADVERTISEMENT

27	1st PRE-BID JOBSITE MEETING W/ PRIMES 28	2nd PRE-BID JOBSITE MEETING W/ PRIMES 29	RFI DEADLINE
30	PROJECT BID DATE

31	CUSD REVIEW BID PACKAGES

32	BOARD AGENDA INFORMATION 33	BOARD APPROVAL
34	DSA APPROVED PLANS

35	ISSUE PRIME-CONTRACTS

1 day	Thu 2/23/23

5 days	Wed 2/8/23

5 days	Fri 2/10/23

1 day	Wed 2/15/23

1 day	Thu 2/16/23

4 days	Fri 2/24/23

1 day	Thu 3/2/23

5 days	Thu 3/2/23

10 days Wed 3/1/23

1 day	Wed 3/15/23

1 day	Wed 3/15/23

10 days Thu 3/16/23

Thu 2/23/23

Tue 2/14/23

Thu 2/16/23

Wed 2/15/23

Thu 2/16/23

Wed 3/1/23

Thu 3/2/23

Wed 3/8/23

Tue 3/14/23

Wed 3/15/23

Wed 3/15/23

Wed 3/29/23

23SS+10 days

25SS+2

days
26SS+3 days

30SS

32

32

33

BIDDER PREQUALIFICATION PACKAGE DUE

FIRST ADVERTISEMENT

SECOND ADVERTISEMENT

1st PRE-BID JOBSITE MEETING W/ PRIMES

2nd PRE-BID JOBSITE MEETING W/ PRIMES

RFI DEADLINE PROJECT BID DATE

CUSD REVIEW BID PACKAGES

BOARD AGENDA INFORMATION

BOARD APPROVAL

DSA APPROVED PLANS

ISSUE PRIME-CONTRACTS

36	CUSD LETTER OF INTENT

37	INCREMENT 2 CONSTRUCTION PHASE OVERVIEW

1 day	Fri 3/17/23

385 days Thu 2/16/23

Fri 3/17/23	33SS+2 Wed 8/7/24	days

CUSD LETTER OF INTENT

38	M - E - P & FS SUBMITTALS	20 days Fri 3/17/23	Thu 4/13/23	36SS	M - E - P & FS SUBMITTALS

39	HVAC PROCUREMENT

40	ELECTRICAL PROCUREMENT

220 days Fri 3/17/23

255 days Fri 3/17/23

Thu 1/18/24	38SS

Thu 3/7/24	38SS

3/17	HVAC PROCUREMENT	1/18

3/17	ELECTRICAL PROCUREMENT	3/7

41	STRUCT. STEEL SHOP DRAWINGS 42	A/E REVIEW APPROVAL
43	M-E-P & FIRE COORDINATION 44	STEEL PROCUREMENT
45	FABRICATION

20 days Fri 3/17/23

10 days Fri 3/31/23

20 days Fri 4/7/23

20 days Fri 4/21/23

20 days Fri 5/5/23

Thu 4/13/23

Thu 4/13/23

Thu 5/4/23

Thu 5/18/23

Thu 6/1/23

38SS

41SS+10

days
42SS+5

days
43SS+10

days
44SS+10 days

STRUCT. STEEL SHOP DRAWINGS

A/E REVIEW APPROVAL

M-E-P & FIRE COORDINATION

STEEL PROCUREMENT

FABRICATION

Page 2

	Mode	
47
51
55
63
6/5	6/3
3/7	4/15
3/11	4/29
9/25	10/
5/14	6/10
Rebid AD-3

CLOVIS UNIFIED	NEW CLOVIS ELEMENTARY FOWLER / McKINLEY	BUSH / DARDEN

ID	Task	Task Name	Duration	Start	Finish	Predecessors	Qtr 4, 2022 Oct	Nov
46	E - BUILDING CONSTRUCTION	307 days Mon 4/17/23	Tue 6/18/24

Qtr 1, 2023 Dec	Jan	Feb

Qtr 2, 2023	Qtr 3, 2023

Mar	Apr	May	Jun	Jul	Aug	Sep

E - BUILDING CONSTRUCTION

Qtr 4, 2023 Oct	Nov

Qtr 1, 2024 Dec	Jan	Feb

Qtr 2, 2024 Mar	Apr	May

Qtr 3, 2024
Jun	Jul	Aug	Sep

47	STEEL ERECTION

48	HVAC START-UP

20 days Mon 6/5/23

105 days Wed 11/22/23

Fri 6/30/23

Tue 4/16/24

46SS+35 days

STEEL ERECTION0

11/22	HVAC START-UP	4/16

2/2	4/8
49	ELECTRICAL POWER-UP	47 days Fri 2/2/24	Mon 4/8/24	ELECTRICAL POWER-UP

50	A - BUILDING CONSTRUCTION 51	STEEL ERECTION
52	HVAC START-UP

53	ELECTRICAL POWER-UP

54	B - BUILDING CONSTRUCTION 55	STEEL ERECTION
56	HVAC START-UP

57	ELECTRICAL POWER-UP

58	C - BUILDING CONSTRUCTION 59	STEEL ERECTION
60	HVAC START-UP

61	C - BUILDING ELECTRICAL POWER-UP 62	D - BUILDING CONSTRUCTION
63	STEEL ERECTION

320 days Wed 5/10/23

20 days Mon 7/3/23

98 days Tue 12/12/23

28 days Thu 3/7/24

300 days Fri 6/2/23

20 days Mon 7/31/23

95 days Mon 12/25/23

36 days Mon 3/11/24

292 days Fri 6/23/23

20 days Mon 8/28/23

116 days Wed 1/24/24

36 days Tue 5/14/24

271 days Fri 7/14/23

20 days Mon 9/25/23

Tue 7/30/24

Fri 7/28/23

Thu 4/25/24

Mon 4/15/24

Thu 7/25/24

Fri 8/25/23

Fri 5/3/24

Mon 4/29/24

Mon 8/5/24

Fri 9/22/23

Wed 7/3/24

Tue 7/2/24

Fri 7/26/24

Fri 10/20/23

46SS+17 days

48SS+14

days
49SS+24

days
50SS+17 days

52SS+9

days
53SS+2

days
54SS+15 days

56SS+22

days
57SS+46

days
59
58SS+15 days

7/3	7/2
A - BUILDING CONSTRUCTION STEEL ERECTION8

12/12

7/31	8/2
B - BUILDING CONSTRUCTION STEEL ERECTION5

12/25

8/28	9/2
C - BUILDING CONSTRUCTION STEEL ERECTION2

D - BUILDING CONSTRUCTION

STEEL ERECTION20

HVAC START-UP	4/25 ELECTRICAL POWER-UP

HVAC START-UP	5/3 ELECTRICAL POWER-UP

HVAC START-UP	7/3

5/14	7/2
C - BUILDING ELECTRICAL POWER-UP

64	HVAC START-UP

65	ELECTRICAL POWER-UP

90 days Wed 2/14/24

20 days Tue 5/14/24

Tue 6/18/24

Mon 6/10/24

61SS
60SS+15 days

2/14	HVAC START-UP	6/18

ELECTRICAL POWER-UP

66	K - BUILDING CONSTRUCTION 67	STEEL ERECTION
68	HVAC START-UP

69	ELECTRICAL POWER-UP

271 days Fri 8/4/23

20 days Mon 10/23/23

100 days Thu 2/22/24

36 days Tue 5/21/24

Fri 8/16/24

Fri 11/17/23

Wed 7/10/24

Tue 7/9/24

62SS+15 days

64SS+6

days
65SS+5 days

0/23	11/
K - BUILDING CONSTRUCTION 1 STEEL ERECTION17

2/22

HVAC START-UP	7/10

5/21	7/9
ELECTRICAL POWER-UP

Page 3

Portables
& Kindergarten
BUILDING A
MIC
WP SPEAKER
TAMPER & FLOW
TAMPER & FLOW
BUILDING P
N. Fowler Ave.
N. Millard Ave.
Z:\Clients\Darden Architects\22066 - CUSD Fowler-McKinley ES\CAD Files\22066 - Elec General & Site Backcheck.dwg
Project
R
3/24/2023 3:03:32 PM
X/E501
48"
48"
BUILDING C
02-120543
1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17	18	19	20

F Po
	Future Portablese rtabl
	
es

POWER
ON

AL ARM
SUPERVISORY
SYSTEM
TROUBLE
GROUND
FAULT

				90" MIN.	6" MIN.
		
CEILING LINE

AUDIO/VISUAL & VISUAL-ONLY DEVICES
								
					96" MAX. AT TOP OF LENS

												
WALL MOUNTED APPLIANCES SHALL HAVE THEIR BOTTOMS AT HEIGHTS ABOVE THE FINISHED FLOOR OF NOT LESS THAN 80" (2m), AND TOPS NO GREATER THAN 96" (2.4m).

TO TOP OF LEVER

MANUAL PULL STATION
LOCAL OPERATING CONSOLE WITH ANNUNCIATOR & MICROPHONE
FLOOR LINE
	80" MIN. AT BOTTOM OF LENS

								

E. Weldon Ave.

R

Q

P

FA CONTROL
SPRINKLER RISER	PANEL "FCP-P"

SWITCH	SPRINKLER RISER
BUILDING K1	FA CONTROL	TAMPER & FLOW SWITCH
Transitional Kindergarten	PANEL "FCP-K1"	BUILDING P
BUILDING K1	SPRINKLER POST
K/TK	Portables	INDICATOR VALVE SPRINKLER RISERBUILDING K2

Transitional Kindergarten

& Kindergarten
SWITCH	BUILDING K2	LOCATION (TYP.)	WP	WP

BUILDING B
Classrooms
uilding
FA CONTROL	K/TK	SPRINKLER RISER	B Lower Grade B PANEL "FCP-K"                                                                                                               TAMPER & FLOW                       Lower Grade

SPRINKLER POST	SWITCH	Classrooms INDICATOR VALVE

WP SPEAKER	FA CONTROL LOCATION (TYP.)	PANEL "FCP-B"
DOUBLE DETECTOR	WP

CHECK VALVE	FA LOCAL OPERATING	WP SPEAKER CONSOLE W/ ANN &                                                                                                                        LOCATION (TYP.)
Administration
BUILDING A Administration

FIRE ALARM GENERAL NOTES

1.      FIRE ALARM SYSTEM: ADDRESSABLE, CLASS B, AUTOMATIC WITH EMERGENCY VOICE/ALARM COMMUNICATION (EVAC).

2.      ALL WORK SHALL CONFORM TO THE 2016 EDITION OF NFPA 72, AND THE 2019 EDITION OF CBC, CEC, AND CFC.

3.     INSTALLATION OF THE FIRE ALARM SYSTEM (FAS) SHALL NOT BE STARTED UNTIL DETAILED DESIGN DOCUMENTS AND SPECIFICATIONS, INCLUDING STATE FIRE MARSHAL LISTING NUMBERS FOR EACH COMPONENT OF THE SYSTEM HAS BEEN APPROVED BY DSA.

4.     UPON COMPLETION OF THE INSTALLATION OF THE FIRE ALARM SYSTEM, A SATISFACTORY TEST OF THE ENTIRE SYSTEM SHALL BE MADE IN THE PRESENCE OF A DSA PROJECT INSPECTOR. (THE LOCAL FIRE AUTHORITY MAY WITNESS THE TEST).

5.      A STAMPED SET OF APPROVED FIRE ALARM DESIGN DOCUMENTS SHALL BE ON THE JOB SITE AND USED FOR THE INSTALLATION.

6.      ANY DISCREPANCIES BETWEEN THE DRAWINGS AND THE CODE OR RECOGNIZED STANDARDS SHALL BE BROUGHT TO THE ATTENTION OF DSA AND THE ARCHITECT/ENGINEER OF THE PROJECT.

7.      DSA, ARCHITECT/ENGINEER AND OWNER SHALL BE NOTIFIED A MINIMUM OF 48 HOURS PRIOR TO THE FINAL INSPECTION AND/OR TESTING.

8.      ALL PENETRATIONS THROUGH RATED ASSEMBLIES REQUIRING OPENING PROTECTION SHALL BE PROVIDED WITH A PENETRATION FIRE STOP SYSTEM AS IDENTIFIED IN CBC CHAPTER 7, UL, OR OTHER LAB TESTING CRITERIA. APPROVED TYPE OF MATERIALS SHALL
WP	BE IDENTIFIED WITHIN THE SPECIFICATION WITHIN THE FIRE ALARM SECTION.

9.     MICROPHONE ASSOCIATED WITH EMERGENCY VOICE ALARM COMMUNICATION SYSTEMS (EVAC) SHALL BE ACCESSIBLE FOR USE, INSTALLED IN COMPLIANCE WITH CBC SECTIONS 11B-305 AND 11B-308.

10. WALL MOUNTED VISUAL NOTIFICATION DEVICES SHALL HAVE THEIR ENTIRE LENS WITHIN AT 80" MINIMUM AND 96" MAXIMUM FROM

UP	FINISHED FLOOR.

FIRE ALARM SYMBOL SCHEDULE

SYMBOL DESCRIPTION	EQUIPMENT

MASTER FIRE ALARM CONTROL PANEL	GAMEWELL-FCI E3 SERIES, FOCAL POINT INTEGRATED, W/ EMERGENCY VOICE/ALARM	W/ ILI-MB-E3, RPT-E3-UTP, FSL-E3, ASM-16, INI-VGC, PM-9, COMMUNICATION	LCD-E3, AM-50-70, DACT-E3;
TELULAR "TELGUARD" TG-7FS INTERNET/5G COMMUNICATOR

LOCAL OPERATING CONSOLE	GAMEWELL-FCI E3-LOC W/ NGA, ASM-16, INI-VGC, W/ ANNUNCIATOR & PAGING MICROPHONE	INCC-MIC

NETWORK FIRE ALARM CONTROL PANEL	GAMEWELL-FCI E3 SERIES W/ ILI-MB-E3, RPT-E3-UTP, W/ EMERGENCY VOICE/ALARM	FSL-E3, INI-VGC, PM-9, LCD-E3, AM-50-70 COMMUNICATION

SMOKE DETECTOR, PHOTOELECTRIC	GAMEWELL-FCI #ASD-PL2F DETECTOR BASE	GAMEWELL-FCI #B501

HEAT DETECTOR	GAMEWELL-FCI #ATD-L2F DETECTOR BASE	GAMEWELL-FCI #B501

FIRE/CARBON-MONOXIDE DETECTOR	GAMEWELL-FCI #MCS-COF SOUNDER BASE	GAMEWELL-FCI #B200S
LOCATE ADJACENT TO THE SUPPLY AIR REGISTER NEAREST TO THE SERVING HVAC UNIT.

PULL STATION	GAMEWELL-FCI #MS-7

CSFM

7165-1703:0125

7300-1402:0504

7165-1703:0125

7165-1703:0125

7272-1703:0121 7300-1653:0109

7270-1703:0115 7300-1653:0109

7275-1703:0175 7135-1653:0213

7150-1703:0109

1	FOR BIDDING ONLY

D
-NOT FOR CONSTRUCTION-

Agency Approval

R

Q

P

N

M

L

K

J

H

SPRINKLER POST INDICATOR VALVE

SPRINKLER RISER TAMPER & FLOW SWITCH

WP

SPRINKLER POST  

INDICATOR VALVE
BUILDING C Upper Grade
Classrooms
Upper Grade Classrooms

utur
WP

MASTER FA CONTROL PANEL "FCP-A"

SPRINKLER RISER TAMPER & FLOW SWITCH

WP

FA CONTROL PANEL "FCP-C"

WP SPEAKER LOCATION (TYP.)

Building D
BUILDING D Upper/ Lower Grade
Classrooms
Upper/ Lower Grade Classrooms

BUILDING E MPR

SPRINKLER RISER TAMPER & FLOW SWITCH

UP

FA CONTROL PANEL "FCP-E"

WP

SPRINKLER POST INDICATOR VALVE
FA CONTROL PANEL "FCP-D"

SPRINKLER RISER TAMPER & FLOW SWITCH

SPRINKLER POST INDICATOR VALVE

11. WALL MOUNTED AUDIBLE NOTIFICATION DEVICES SHALL HAVE THEIR TOPS MOUNTED AT 90" MINIMUM AND 100" MAXIMUM FROM FINISHED FLOOR AND NO CLOSER THAN 6" TO A HORIZONTAL STRUCTURE.

12. AUDIBLE DEVICES SHALL PROVIDE A SOUND PRESSURE LEVEL OF 15 DECIBELS (dBA) ABOVE THE AVERAGE AMBIENT SOUND LEVEL OR 5 dBA ABOVE THE MAXIMUM SOUND LEVEL HAVING A DURATION OF AT LEAST 60 SECONDS, WHICHEVER IS GREATER, IN EVERY SPACE WITHIN A BUILDING THAT MAY BE OCCUPIED AND BE INTELLIGIBLE.

13. AUDIBLE DEVICES SHALL BE SYNCHRONIZED TEMPORAL CODE 3 PATTERN, PRIOR TO "EVAC" ANNOUNCEMENT. THE CARBON MONOXIDE SIGNAL SHALL SOUND A FOUR-PULSE TEMPORAL PATTERN PER NFPA 720, 5.8.6.5.1.

14. THE CONTRACTOR SHALL ADJUST/INSTALL ALL DEVICES TO MAXIMIZE PERFORMANCE AND TO MINIMIZE FALSE ALARMS.

15. VISUAL DEVICES SHALL NOT EXCEED 2 FLASHES PER SECOND AND SHALL NOT BE SLOWER THAN 1 FLASH PER SECOND. THE DEVICE SHALL HAVE A PULSING LIGHT SOURCE NOT LESS THAN 15 CANDELA. VISUAL DEVICES WITHIN 55' FROM EACH OTHER SHALL BE SYNCHRONIZED.

16. UNDERGROUND AND EXTERIOR CONDUITS SHALL HAVE WATERTIGHT FITTINGS AND WIRE APPROVED FOR WET LOCATIONS.

17. ALL FIRE ALARM WIRING SHALL BE FLP OR FPLP (FIRE POWER LIMITED OR FIRE POWER LIMITED PLENUM) AS REQUIRED FOR APPLICATION. WIRING IN CONDUIT ABOVE GROUND MAY BE THHN OR THWN.

18. PER CEC STANDARDS, ALL WIRING SHALL BE PULLED THROUGH EACH JUNCTION BOX AND CONNECTED DIRECTLY TO EACH FIRE DEVICE. DO NOT SPLICE WIRE. ANY CONNECTION SHALL BE BY LUG CONNECTION AT A DEVICE OR AT A FATC TERMINAL BLOCK ONLY. ALL BOXES TO BE SIZED PER CEC.

19. SMOKE DETECTORS SHALL NOT BE CLOSER THAN 12" FROM FIRE SPRINKLERS NOR 36" FROM SUPPLY AIR DIFFUSERS. IN AREA OF CONSTRUCTION OR POSSIBLE DAMAGE/CONTAMINATION, NEWLY INSTALLED FIRE ALARM DEVICES SHALL BE COVERED UNTIL THAT AREA IS READY TO BE TURNED OVER TO THE OWNER.

20. ALL FIRE ALARM CIRCUITS SHALL BE IN CONDUIT, SURFACE RACEWAY, OR OPEN RUN ABOVE CEILINGS, UNDER FLOORS, AND IN WALLS IN A NEAT AND PROTECTED MANOR AS INDICATED ON DESIGN DOCUMENTS. EXPOSED CIRCUITS ARE ONLY PERMITTED WHEN NOTED AS EXPOSED ON DESIGN DOCUMENTS. OWNER STANDARDS MAY BE MORE STRINGENT.

21. FIRE ALARM PANEL, REMOTES, AND COMPONENTS SHALL BE SECURED TO MOUNTING SURFACES PER MANUFACTURERS' SPECIFICATIONS. ANY SINGLE DEVICE SHALL NOT EXCEED THE WEIGHT OF 20 LBS. WITHOUT SPECIAL MOUNTING DETAILS.

22. A DEDICATED BRANCH CIRCUIT SHALL BE PROVIDED FOR FIRE ALARM EQUIPMENT. THIS CIRCUIT SHALL BE ENERGIZED FROM THE COMMON USE AREA PANEL AND SHALL HAVE NO OTHER OUTLETS. THE BREAKER SHALL HAVE A LOCKING DEVICE WITH RED MARKING PER NFPA 72, SECTION 10.6.5.4 AND 10.6.5.2.3 TO BLOCK THE HANDLE IN THE "ON" POSITION. THE CIRCUIT BREAKER SHALL BE LABELED "FIRE ALARM CIRCUIT CONTROL". CIRCUIT ID TO BE LABELED AT THE FIRE PANEL/EXTENDERS.

23. THE INSTALLING CONTRACTOR SHALL PROVIDE A RECORD OF COMPLETION IN COMPLIANCE WITH NFPA 72, SECTION 7.5.6.

24. CONTROL PANELS AND REMOTE ANNUNCIATORS SHALL BE INSTALLED WITH THEIR BOTTOMS MOUNTED AT 48".

25. THE INSTALLING CONTRACTOR SHALL PROVIDE SYSTEM PROGRAMMING FOR SUPERVISORY MONITORING PER CBC 901.6.2.

26. SUPERVISORY MONITORING SHALL BE TESTED AND VERIFIED AS SENDING CORRECT SIGNALS IN CONJUNCTIONS WITH FINAL TEST. FIRE ALARM SYSTEMS SHALL TRANSMIT THE ALARM, SUPERVISORY AND TROUBLE SIGNALS TO AN APPROVED SUPERVISING STATION IN ACCORDANCE WITH NFPA 72. THE SUPERVISING STATIONS SHALL BE LISTED AS EITHER UUFX (CENTRAL STATION) OR UUJS (REMOTE AND PROPRIETARY) BY UNDERWRITERS LABORATORY (UL) OR SHALL COMPLY WITH THE REQUIREMENTS OF STANDARD FM 3011. A COPY OF ALL DEVICES REPORTED TO THE CENTRAL STATION SHALL BE PROVIDED TO THE OWNER'S ELECTRONICS DEPARTMENT.

27. OWNER SHALL BE RESPONSIBLE FOR ESTABLISHING A FIRE SYSTEM MONITORING CONTRACT OR PROVISIONS.

28. ALL WIRING IS SHOWN DIAGRAMMATICALLY. SUBJECT TO DSA APPROVAL, CONTRACTOR MAY VARY SEQUENCE OF CIRCUITRY; HOWEVER, ALL CIRCUITS SHALL BE CONTINUOUS AND SUPERVISED.

29. ALL CONNECTIONS SHALL BE PROPERLY LABELED BY CONDUCTOR AND SHALL HAVE STA-KON LUG CONNECTORS. PANDUIT TAG (TIE

WRAP) SEPARATELY.

MONITOR MODULE

RELAY MODULE

VISIBLE NAC DEVICE, CEILING MT'D (cd INDICATED ON PLANS)

SPEAKER/VISIBLE NAC DEVICE, CEILING MT'D (WATTS & cd INDICATED ON PLANS)

SPEAKER/VISIBLE NAC DEVICE, WALL MT'D (WATTS & cd INDICATED ON PLANS)

EXTERIOR SPEAKER, WP, WALL MT'D (WATTS INDICATED ON PLANS)

SPRINKLER POST INDICATOR VALVE

DOUBLE DETECTOR CHECK VALVE

SPRINKLER RISER TAMPER SWITCH

SPRINKLER RISER FLOW SWITCH

SPRINKLER RISER BELL

GAMEWELL-FCI #AMM-2F

GAMEWELL-FCI #AOM-2SF

EATON/WHEELOCK #ELSTWC

EATON/WHEELOCK #ELSPSTWC

EATON/WHEELOCK #ELSPSTR

EATON/WHEELOCK #ET-1010-R

SPECIFIED BY FIRE PROTECTION ENG.

SPECIFIED BY FIRE PROTECTION ENG.

SPECIFIED BY FIRE PROTECTION ENG.

SPECIFIED BY FIRE PROTECTION ENG.

SPECIFIED BY FIRE PROTECTION ENG.

7300-1703:0102

7300-1703:0102

N 7135-0785:0504

7320-0785:0505

7320-0785:0505

7320-0785:0105	M

L

K

J

H

30. FIRE ALARM TERMINAL CABINETS SHALL HAVE SUFFICIENT SPACE, TERMINAL BOARDS AND SCREW TERMINAL CONNECTORS TO ALLOW CONNECTION OF ALL CONDUCTORS SHOWN. PROVIDE BARRIER TO SEPARATE FIRE ALARM SYSTEM WHEN TERMINAL CABINET IS SHARED WITH NON-FIRE ALARM SYSTEMS. CONTRACTOR SHALL BE REQUIRED TO SUBMIT WITH HIS OTHER SHOP DRAWINGS DETAILED DRAWINGS OF HIS PROPOSED CONNECTIONS AT EACH FIRE ALARM TERMINAL CABINET PRIOR TO COMMENCING ANY WORK.

31. ALL NAC CIRCUIT CONDUCTORS SHALL BE #12 AWG, STRANDED (19 STRANDS OR LESS) COPPER, UNLESS OTHERWISE NOTED.

G	32. SET END-OF-LINE RESISTORS IN DISTRIBUTION TERMINAL CABINETS. 33. BATTERIES SHALL BE STAMPED WITH DATE OF MANUFACTURE.

34. INSTALLATION OF FAS EQUIPMENT SHALL BE BY AN AUTHORIZED ENGINEERED SYSTEM DISTRIBUTOR FOR THE EQUIPMENT SPECIFIED BY THE MANUFACTURER FOR SALES, SERVICE, INSTALLATION AND MAINTENANCE. PROVIDE CERTIFICATIONS WITH EQUIPMENT SUBMITTALS. SUBMITTALS BY FIRMS NOT FULFILLING THIS REQUIREMENT WILL BE AUTOMATICALLY REJECTED.

35. THE FAS INSTALLER SHALL BE NICET LEVEL 2 CERTIFIED.

36. THE FAS INSTALLER SHALL PROVIDE ALL FACTORY WARRANTIES TO THE OWNER AT THE CLOSE UP OF THE PROJECT.

F                                                                                                                                                                                                                                                                                                              37. THE FAS INSTALLER SHALL PROVIDE WRITTEN CERTIFICATION USING NFPA 72 INSPECTION AND TESTING FORMS AND SHALL CERTIFY THAT THE INSTALLATION, TESTING, AND OPERATION CONFORM IN ALL RESPECTS TO THE REQUIREMENTS AS SET FORTH IN TITLE 19

OF THE CALIFORNIA CODE OF REGULATIONS AND PART 3, ARTICLE 760 OF TITLE 24 OF THE C.C.R. AND C.B.C. SECTION 907. THE CONTRACTOR SHALL SUBMIT THE COMPLETED FAS CERTIFICATION AND DESCRIPTION FORM TO DIVISION OF STATE ARCHITECT.

INITIATION CONDITON

ACTION
	FIRE SPRINKLER TAMPER SWITCH, POST INDICATOR VALVE
	CARBON-MONOXIDE (CO) DETECTOR END OF LIFE
	CARBON-MONOXIDE (CO) DETECTOR ALARM
	SMOKE, HEAT, OR DUCT DETECTOR, FIRE SPRINKER FLOW SWITCH
	POWER LOSS, SHORT CIRCUIT, GROUND FAULT
	
ANNUNCIATE TROUBLE
						
ANNUNCIATE ALARM
						
ANNUNCIATE CO ALARM
						
ANNUNCIATE SUPERVISORY
						
INITIATE NOTIFICATION APPLICANCES
						
INITIATE EV/AC APPLICANCES
						
TRANSMIT TO CENTRAL STATION
						
CLOSE FIRE/SMOKE DAMPER
						
SHUTDOWN HVAC UNITS
						
DOOR RELEASE
						
ACCESS CONTROL OVERRIDE

General Notes

F13	Fire Alarm Sequence of Operations Matrix

G

F

E

F1	Fire Alarm Reference Site Plan 1" = 60'-0"

D

N	38. INCLUDE ALL DEMOLITION OF EXISTING FIRE ALARM SYSTEM WHETHER SPECIFICALLY SHOWN OR NOT. REMOVE ALL CABLING &	No Scale UNUSED EXPOSED RACEWAY & OUTLETS. BLANK OFF ALL UNUSED WALL & HARD CEILING OUTLETS. REMOVE ALL UNUSED OUTLETS
IN TEE-BAR CEILING & REPLACE ACOUSTIC TILES.      RETURN ALL DEVICES, APPLIANCES, & CONTROL PANELS TO OWNER IF REQUESTED BY OWNER DURING CONSTRUCTION.

39. WHEN FIRE ALARM WORK WILL DISABLE PORTIONS OF THE EXISTING FAS, PROVIDE ALL REQUIRED OVERTIME AND FIRE WATCH IN SCOPE OF WORK.

40. WHERE FIRE ALARM DEVICES ARE BEING INSTALLED IN OTHERWISE INACCESSIBLE AREAS, PROVIDE AN ALLOWANCE FOR THE INSTALLATION OF ACCESS PANELS AND ALL WORK ASSOCIATED WITH THE INSTALLATION. THE CONTRACTOR SHALL CUT ALL THE OPENINGS. THE SIZE OF THE ACCESS PANEL SHALL BE DETERMINED BY THE MAN ACCESS REQUIREMENTS. PROVIDE PAINT GRADE ACCESS DOORS AND PAINT TO MATCH THE COLOR & SHEEN OF THE EXISTING CEILING.

41. FIRE ALARM SYSTEM INSPECTION, TESTING, AND MAINTENANCE SHALL COMPLY WITH NFPA 72, CHAPTER 14.

42. PROVIDE FIRE ALARM RECORD DOCUMENTS CABINET NFPA 72, 7.7.2

- EVERY NEW FIRE ALARM SYSTEM SHALL PROVIDE A DOCUMENTATION CABINET, INSTALLED AT THE SYSTEM CONTROL PANEL OR OTHER APPROVED LOCATION.
- THE DOCUMENTATION CABINET SHALL BE PROMINENTLY LABELED, "FIRE ALARM SYSTEM RECORD DOCUMENTS". - ALL RECORD AND TESTING DOCUMENTATION SHALL BE STORED IN THE CABINET.
- CONTENTS SHALL BE ACCESSIBLE BY AUTHORIZED PERSONNEL ONLY.

- WHERE CABINET IS INSTALLED IN A LOCATION OTHER THAN THE SYSTEM CONTROL UNIT, ITS LOCATION SHALL BE IDENTIFIED AT THE SYSTEM CONTROL UNIT.

PROVIDE SYSTEM DOCUMENTS AS APPLICABLE:

AUDIBLE DEVICES: WHERE CEILING HEIGHTS PERMIT WALL-MOUNTED APPLIANCES SHALL HAVE THEIR TOPS AT HEIGHTS ABOVE FINISHED FLOORS OF NOT LESS THAN 90" (2.30 M) AND BELOW THE FINISHED
CEILINGS OF NOT LESS THAN 6" (0.15m).

R
Hardin-Davidson Engineering	E17850 356 Pollasky Ave., Suite 200, Clovis, CA 93612
559.323.4995 tel ● 559.323.4928 fax
www.hardin-davidson.com	Consultant

McKinley/Fowler Elementary School Clovis Unified School District
Fresno, CA 93727

Fire Alarm System

Symbols, Site Plan, Notes, and Details

Drawing

E

D

C

B

- RECORD DRAWINGS/AS-BUILTS

- EQUIPMENT CUT SHEETS & CA SFM LISTINGS - ALTERNATIVE MEANS AND METHODS
- PERFORMANCE BASED DESIGN DOCUMENTATION (NFPA 72, 7.3.7)

- SYSTEM RECORD OF COMPLETION & ANY SUPPLEMENTAL INSPECTION AND TESTING DOCUMENTATION (NFPA 72, 7.8.2) - EMERGENCY RESPONSE PLAN (NFPA 72, 7.3.8)
- EVALUATION DOCUMENTATION (NFPA 72, 7.3.9)

- RISK ANALYSIS DOCUMENTATION (NFPA 72, 7.3.6)

- SOFTWARE & FIRMWARE CONTROL DOCUMENTATION (NFPA 72, 23.2.2)

FIRE ALARM CABLING INSTALLATION NOTES

1.      FIRE ALARM CABLING SHALL BE INSTALLED IN A RACEWAY SYSTEM, EXCEPT AS NOTED BELOW.

Architect

No.	Revision/Submission

3	Addendum 3- Electrical Rebid

. 23724
No. C37102	C

Date 03/28/23

B

2.     IT SHALL BE ACCEPTABLE TO INSTALL FIRE ALARM CABLING FOR SLC, NAC, EV/AC, AND FA NETWORK OPEN AIR IN ATTIC SPACES ABOVE T-BAR CEILINGS. FIRE ALARM CABLING SHALL BE INSTALLED ON DEDICATED J-HOOKS, SEPARATE FROM OTHER SYSTEMS, PER DETAIL M13/X/E401.

3.      WHEREVER A HARD LID CEILING SYSTEM IS PRESENT, THE FIRE ALARM CABLING SHALL BE INSTALLED IN CONDUIT IN THE ATTIC SPACE ABOVE THE CEILING.

A	4.     FA FIBER OPTIC NETWORK CABLING SHALL BE RUN DIRECTLY FROM FCP NODE TO FCP NODE (NOT PATCHED IN FROM MDF/IDF) IN A STYLE 7 CONFIGURATION WITH ARMORED, 6-STR SINGLEMODE FIBER OPTIC CABLE. PROVIDE A 1 1/2" CONDUIT STUB FROM THE TOP OF EACH CONTROL PANEL TO THE HORIZONTAL LADDER RACK ABOVE FOR BRINGING THE FO CABLE INTO THE CABINET. TERMINATE
ALL STRANDS SUCH THAT THEY ARE READY TO USE.

Revision

Designed By:      SD Copyright 2022 Darden Architects

	 Scale:	As indicated Drawn By:	HDE	A

A13	Fire Alarm Wall Mounted Devices Elevation	Project Number:     2116 Checked By:       SD
No Scale	Date:	09/19/2022 Reviewed By:     SD     Sheet: 	         of: 	

1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17	18	19		20 AD3- EX01

AH-8
INV-A
AH-8
+44"
+44"
1
31
8
12
+44"
Z:\Clients\Darden Architects\22066 - CUSD Fowler-McKinley ES\CAD Files\22066 - Elec Buildings Backcheck.dwg
R
R
3/23/2023 1:48:38 PM
02-120543
1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17	18	19	20

R

1	FOR BIDDING ONLY
D
-NOT FOR CONSTRUCTION-

R

Q

XFMR "TAL"

PANEL                                       "LCP-A"PANEL "AL"                                                           "AH"
Electrical Room

120
AL-39

Agency Approval

KEYNOTES
Q

P

1	2	3	4	5	6	7	8	9	10

15 +24"

13 +78"

ALIT-2/4

1	14-30R

17
+45"       Telecom Room 104
ALIT-13,15,17

ALIT-1,3

ALIT-6/8

3       14-30R

1.      3/4" THICK x 8' HIGH, FIRE-RESISTANT PLYWOOD BACKBOARD. PAINTED WITH FIRE RESISTANT PAINT. SECURE PLYWOOD TO (2) METAL STUDS WITH #10 x 4" GALVANIZED FLAT HEAD SMS AT 8" CENTERS. WITH MIN. (4) SCREWS AT 6" CENTERS AT EACH WALL STUD. WITH MIN. 2 1/2" EMBEDMENT INTO WALL STUD.

2.     PROVIDE TELECOM GROUND BUS PER DETAIL N8/X/E401 AND J8/X/E401.

3.     EMERGENCY LIGHTING INVERTER PER DETAIL H14/X/E202.
P

4.     CONNECT POWER TO FA, EMS, SECURITY SYSTEMS AND LIGHTING

GATEWAY.

PANEL ALIT-10,12,14,16	"ALIT"

5.     PAD MOUNTED TRANSFORMER. SEE DETAIL D10/X/E301 FOR MOUNTING.

SEE POWER SINGLE LINE DIAGRAM G10/X/E301.

N

A

M

B

+44"
29	27 L
C	 27 +44"

+45"
29  

Toilet 112a

K	D

29
Nurse

112

29

27

27

29

+44"

7	AL-49

AL-1,3,5,7	(TYP.)	AL-41

1	3		5	7 Main Office
(TYP.)	100

3	1	AL-42/44 5  

7	7

2       4	+44" 4

4	AL-18

2	CEILING

Library Open Area

113

Reading 113a

6

M14 1/4" = 1'-0"

B

C

D

16        14                    12                    10 +78"     +78"                 +78"                 +78"

5
+24"     11       +24"       9	7        +24"	+24"

ALIT-5,7,9,11

Building A - Enlarged Power Plan

6.      WALL MOUNTED PANELBOARD. SEE DETAIL L1/X/E302 FOR MOUNTING. SEE POWER SINGLE LINE DIAGRAM G10/X/E301.

11. SEE TEACHING WALL ELEVATION DETAIL K1/X/E402.

12. MOUNT DEVICE(S) INSIDE CASEWORK. SEE ARCHITECTURAL FOR EXACT LOCATION AND ADDITIONAL DETAIL.

13. 12/3 MC POWER AND 16/2 MC CONTROL. SNAKE THROUGH WINDOW SYSTEM TO DOOR OPENER/ CONTROLLER. VERIFY REQUIREMENT WITH VENDOR PRIOR TO ROUGH-IN.

14. 1/2"C. 16/2 TO DOOR PUSH BUTTON. VERIFY DOOR PUSH BUTTON LOCATION WITH ARCHITECT. VERIFY REQUIREMENT WITH VENDER PRIOR TO ROUGH-IN.

15. POWER SUPPLY CABINET WITH HINGED CONSOLE AND LOCK HASP AT +96" TO BOTTOM. VERIFY REQUIREMENT WITH VENDER PRIOR TO ROUGH-IN.

16. POWER       OUTLET       FOR       PROJECTOR.       VERIFY       LOCATION       OF PROJECTOR/MOUNT WITH FACTORY DATA IN RELATION TO SCREEN PRIOR TO ROUGH-IN. MOUNT PROJECTOR PER DETAIL F1/X/E302.

17. PROVIDE     L5-20R     TWIST-LOCK     POWER     OUTLET     AND     CONNECT MOTORIZED SCREEN. VERIFY LOCATION PRIOR TO ROUGH-IN.

18. MOTORIZED SCREEN FACTORY WALL CONTROLLER. VERIFY LOCATION PRIOR TO ROUGH-IN. VERIFY ALL REQUIREMENT PER MANUFACTURER.

19. PROVIDE ROUGH-IN AT THIS ENTRANCE FOR FUTURE ACCESS CONTROL SYSTEM. PROVIDE CARD READER J-BOX AT +45" AFF WITH 1/2" CONDUIT TO ATTIC SPACE FOR A DOOR CONTACTOR AND AN ELECTRIC STRIKE, (4) TOTAL FOR DOUBLE DOORS. PROVIDE DATA OUTLET AND J-BOX WITH 120V POWER WIRING IN ATTIC SPACE NEAR DOOR FOR FUTURE CONNECTION TO A DOOR CONTROLLER.

20. PROVIDE FLOOR BOX WITH POWER OUTLET, DATA OUTLET, AND A/V INPUTS. SEE LOW VOLTAGE PLAN A1/A/E401 FOR LOW VOLTAGE
SYSTEMS INFORMATION.

N

M

L

K

AL-53 E

F	Fire Riser 119

GIS Office	37 111
25

Office 11

102

9
AL-9,11	31	4

E 8	6      +44"

F

J

+44"
+44"
19		19	23 23

AL-25,	+44" 27,29

Office

+44"	101

2

AL-2,4	4

AL-6,8		J 6
2	6	+44"

G

Workroom     19 110
19

21

23
H                                                                                                                                                                                                                                    AL-19,21,23 19
H	+44"

Hallway 37

118

35

Storage 109

35

33
15	13	DF-1 Hallway                                         15                                             AL-13,15

117	Conference

1
103		13	10      12 +66"3                                                     Hallway
37	15	+44"3	15	116     31

107
WH-1
Custodial	Electrical Room	10 AL-17       AL-35,37       AL-32/34      120       AL-31,33                        AL-10,12
35	12

14

AL-14,16 Roof Access
114a

Library Classroom

114

G 16	14	+44"

8

14

16	H

H

16	Library Storage

+102"	115

G                                                                                                                                                                                                             Staff Restroom 108 +45"

  35 
J

Staff Restroom	37	AL-49

35     106
+45"	37

+44"
+44"
TO ODU-A1	10

AL-46/48
Telecom Room 31
104	12

31
10

14
G

16

J

K

Principal's Office	AL-49

105

K

F	L

SEE ENLARGED PLAN M14/A/E201
FOR THIS AREA.

General Notes

L

F

M	M

E

Hardin-Davidson Engineering	E17850 356 Pollasky Ave., Suite 200, Clovis, CA 93612
559.323.4995 tel ● 559.323.4928 fax
www.hardin-davidson.com	Consultant

E

Project
McKinley/Fowler Elementary School Clovis Unified School District
Fresno, CA 93727

D

1	2	3	4	5	6	7	8	9	10

Building A Power Plan
Drawing

D

No. C23724
C	No. C37102	C

Architect

No.	Revision/Submission

3	Addendum 3- Electrical Rebid

Date

03/28/23

B	B

Revision

Designed By:      SD Copyright 2022 Darden Architects

A 	 Scale:	As indicated Drawn By:	HDE

A1	Building A - Power Plan	Project Number:     2116 Checked By:       SD

1/8" = 1'-0"	Date:	09/19/2022 Reviewed By:     SD

A/E201	A

Sheet: 	         of: 	

1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17	18	19		20 AD3- EX02

+44"
+44"
+44"
+44"
+44"
+44"
Z:\Clients\Darden Architects\22066 - CUSD Fowler-McKinley ES\CAD Files\22066 - Elec Buildings Backcheck.dwg
R
R
3/23/2023 1:50:07 PM
02-120543
1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17	18	19	20

R

Electrical Room 120

Q

1	FOR BIDDING ONLY

D
-NOT FOR CONSTRUCTION-

Agency Approval

KEYNOTES

R

Q

         LAN

LAN     
AT&T	WAN MPOE

Telecom Room

1.      2-POST RACK(S), CABLE MANAGEMENT SECTION, AND APPURTENANCES PER SPECS. SEE DETAIL A13/X/E401 FOR MOUNTING.

2.      CHATSWORTH 11252-71X 12" LADDER RACK SYSTEM PER

SPECIFICATIONS AND DETAIL A1/X/E401.

P

1	2	3	4	5	6	7	8	9	10

NETWORK ELEC-TRONICS

"MDF"

FIBER,	104 COPPER       PA
PATCH       EQT.

(TYP.)

(TYP.)

FA,EMS,SECURITY,

LTG GATEWAY

11. SEE TEACHING WALL ELEVATION DETAIL K1/X/E402.

12. MOUNT DEVICE(S) INSIDE CASEWORK. SEE ARCHITECTURAL FOR EXACT
LOCATION AND ADDITIONAL DETAIL.	P

13. PROVIDE FLOOR BOX WITH DATA OUTLET AND A/V INPUTS.

+72"	+72"

N	N

A

M	M

M14	Building A - Enlarged Low Voltage Plan 1/4" = 1'-0"

+44"
B	B

L		Nurse	(TYP.) C                                                                                       +44"                                           112

L Reading	C

113a

Toilet	(TYP.)

112a

Main Office

100

K	D

E

F	Fire Riser 119
J

+44"

GIS Office

111

Office                                Office 102                                       101

+44"

+44"

D	K Library Open Area

113

E

+44"	F

J +44"

1 1/4"C. G

Workroom H	110

Storage

109

Hallway

117

Conference 103

(2)1 1/4"C.
  +66"

+45"
Roof Access	G 114a

H

H

Hallway

118

Custodial

107

+44"

Electrical Room

120

Hallway

116

Library Classroom

114

H +102"

Library Storage

115

G	Staff Restroom 108

J

K

F	L

Staff Restroom

106

                         Principal's Office

105

Telecom Room 104

SEE ENLARGED PLAN M14/A/E401
FOR THIS AREA.

J

K

General Notes

L

G

F

M	M

E

Hardin-Davidson Engineering	E17850 356 Pollasky Ave., Suite 200, Clovis, CA 93612
559.323.4995 tel ● 559.323.4928 fax
www.hardin-davidson.com	Consultant

E

Project
McKinley/Fowler Elementary School Clovis Unified School District
Fresno, CA 93727

D

1	2	3	4	5	6	7	8	9	10

Building A Low Voltage Plan
Drawing

D

. 23724
No. C37102
C	No. C37102	C

Architect

No.	Revision/Submission

3	Addendum 3- Electrical Rebid

Date

03/28/23

B	B

Revision

Designed By:      SD Copyright 2022 Darden Architects

A 	 Scale:	As indicated Drawn By:	HDE

A1	Building A - Low Voltage Plan	Project Number:     2116 Checked By:       SD

1/8" = 1'-0"	Date:	09/19/2022 Reviewed By:     SD

A/E401	A

Sheet: 	         of: 	

1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17	18	19		20 AD3- EX03

Z:\Clients\Darden Architects\22066 - CUSD Fowler-McKinley ES\CAD Files\22066 - Elec General & Site Backcheck.dwg
Project
R
3/24/2023 3:04:16 PM
(1)D

s1-13
	s
	1-12

	
s1-21      s1-22

H s1-13
	C-s
	B3
1-12

	
s
	H 1-22
	C s
	
s1-21

	WP 2W
		WP 2W

	v1-2 n1-2
		v1-4 n1-3

	
s1-20A
	
s
	
1-21
	
s
	
1-22
	
s
	
1-23
	
s
	
1-24

										

s2-32
	
s
	
2-31

1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17	18	19	20

R

BUILDING P

FIRE ALARM CABLE SCHEDULE

SYMBOL NAME

A	SIGNALING LINE CIRCUIT (SLC) CABLE

DESCRIPTION

16/2 TWISTED PAIR, STRANDED, LOW CAPACITANCE	BUILDING B

1	FOR BIDDING ONLY
02-120543
D
-NOT FOR CONSTRUCTION-

R

120V DEDICATED CIRCUIT (PROVIDE RED HANDLE C.B. W/ LOCK-ON

DEVICE & LABEL PER NFPA 72 SECTION 10.6.5.2, 10.6.5.4.)

WEST PENN #D990

AW	SIGNALING LINE CIRCUIT (SLC) CABLE, OSP

WEST PENN #AQC225

FA POWER LIMITED, RISER CABLE (FPLR)

16/2 TWISTED PAIR, STRANDED, AQUASEAL

FA POWER LIMITED CABLE (FPL)

Agency Approval

120V DEDICATED CIRCUIT (PROVIDE RED HANDLE C.B. W/ LOCK-ON

DEVICE & LABEL PER NFPA 72 SECTION 10.6.5.2, 10.6.5.4.)

Q

NETWORK

	 FIRE ALARM CONTROL
PANEL

'FCP-P'

(1)B, (1)C (TYP.)

v1-1        v1-2        v1-3 n1-1        n1-2        n1-3

75cd         15cd         15cd 1W            1/8W         1/8W

v1-4        v1-5        v1-6 n1-4        n1-5        n1-6

15cd         15cd         75cd 1/8W         1/8W         1W

B	NOTIFICATION APPLIANCE CKT (NAC) CABLE WEST PENN #998S

BW	NOTIFICATION APPLIANCE CKT (NAC) CABLE, OSP WEST PENN #AQ227

C	EM. VOICE/ALARM COMM. (EV/AC) CABLE

WEST PENN #HF995

12/2 TWISTED PAIR, STRANDED

FA POWER LIMITED, RISER CABLE (FPLR)

12/2 TWISTED PAIR, STRANDED, AQUASEAL FA POWER LIMITED CABLE (FPL)

14/2 SHIELDED TWISTED PAIR, STRANDED

FA POWER LIMITED CABLE (FPL)

v1-5

(1)B, (1)C (TYP.)                  WP (2)C           2W

v1-1        v1-2        v1-3        v1-4 n1-1        n1-2        n1-3        n1-4

v1-6        v1-7

n1-5        n1-6

Q

v1-8        v1-9

n1-7        n1-8        n1-9

15cd         30cd         75cd         75cd (1)A (TYP.)	CW	EM. VOICE/ALARM COMM. (EV/AC) CABLE, OSP	14/2 SHIELDED TWISTED PAIR, STRANDED, AQUASEAL	1/4W         1/2W         1W	1W

15cd         15cd         15cd         75cd         75cd 1/2W         1/2W                         1W            1W

s1-1        s1-2        s1-3        s1-4        s1-5        s1-6        s1-7        s1-8        s1-9       s1-10 P

(1)DW

WEST PENN #AQC295

D	INITIATING DEVICE CIRCUIT (IDC) CABLE WEST PENN #994S

DW	INITIATING DEVICE CKT (IDC) CABLE, OSP

WEST PENN #AQC226

FA POWER LIMITED CABLE (FPL)

14/2 TWISTED PAIR, STRANDED

FA POWER LIMITED, RISER CABLE (FPLR)

14/2 TWISTED PAIR, STRANDED, AQUASEAL
FA POWER LIMITED CABLE (FPL)	(1)FW

NETWORK FIRE ALARM CONTROL PANEL
'FCP-B'

v2-2

v2-1        n2-1

v2-6

WP (2)C	4W

v2-3        v2-4        v2-5 n2-2        n2-3        n2-4

v2-7

n2-5       n2-6

P

v2-8        v2-9        v2-10 n2-7        n2-8        n2-9

N
BUILDING K1

F	NETWORK COMM CABLE

FW	SITE NETWORK COMM CABLE

G	POWER CABLE

WEST PENN #998S

ARMORED, 6-STR SM ISP FIBER OPTIC CABLE

ARMORED, 6-STR SM OSP FIBER OPTIC CABLE

12/2 TWISTED PAIR, STRANDED

FA POWER LIMITED, RISER CABLE (FPLR)

WP           15cd         15cd         75cd         75cd         15cd         15cd         15cd         75cd         75cd 2W            1/4W         1/2W         1W            1W            1/2W                         1/8W         1W            1W

(1)A, (1)G (TYP.)

s1-1        s1-2        s1-3        s1-4        s1-5        s1-6        s1-7        s1-8        s1-9       s1-10

HC-B4

s1-19      s1-18      s1-17      s1-16      s1-15      s1-14	s1-11

N

120V DEDICATED CIRCUIT (PROVIDE RED HANDLE C.B. W/ LOCK-ON

DEVICE & LABEL PER NFPA 72 SECTION 10.6.5.2, 10.6.5.4.)

(1)D	HC-B1	(1)A

s2-1        s2-2        s2-3        s2-4

HC-B2

s2-5        s2-6        s2-7        s2-8        s2-9       s2-10

(1)B, (1)C (TYP.)

v1-3        v1-5	(1)FW	BUILDING A

HC-B9	HC-B5

s2-19      s2-18      s2-17      s2-16

HC-B6

s2-15      s2-14      s2-13      s2-12      s2-11

M

NETWORK FIRE ALARM CONTROL PANEL 'FCP-K1'

L	(1)D

v1-1                                 (2)C            v1-7 n1-1                                     v1-6        n1-4

15cd         15cd         75cd         WP           30cd 1/8W         1/8W         1W            1W            1/2W

(1)A, (1)G (TYP.)

s1-1        s1-2        s1-3        s1-4        s1-5

s1-17      s1-16

v1-8	(1)FW n1-5        v1-9

75cd         WP 1W            2W

(2)C

s1-6        s1-7        s1-8        s1-9       s1-10

HC-K1

s1-15      s1-14      s1-13      s1-12      s1-11

WIRELESS CELLULAR (SECONDARY PATH)

ETHERNET
& 5G	CAT6 INTERNET TO MDF (PRIMARY PATH)

COMMUNICATOR

CAT6 DACT
120V DEDICATED CIRCUIT (PROVIDE RED HANDLE C.B. W/ LOCK-ON

DEVICE & LABEL PER NFPA 72 SECTION 10.6.5.2, 10.6.5.4.)

(1)B, (1)C (TYP.)

HC-B8	(1)A	HC-B7	M

(1)DW

L

HC-K2	(1)A (TYP.)

(1)F

v1-1        v1-2        v1-3        v1-4        v1-5        v1-6        v1-7        v1-8 n1-1        n1-2        n1-3        n1-4        n1-5        n1-6        n1-7        n1-8

15cd         30cd         15cd         15cd         15cd         15cd         30cd         15cd 1/4W         1/8W         1/4W         1/8W         1/8W         1/8W         1/4W         1/8W

v1-9        v1-10 n1-9        n1-10

30cd         15cd 1/4W         1/8W

(1)FW

v1-17      v1-16      v1-15      v1-14      v1-13      v1-12      v1-11 n1-17     n1-16     n1-15     n1-14     n1-13     n1-12     n1-11

K

BUILDING K2

FIBER PATCH PANEL WITH RED CONNECTORS AT MAIN IT
ROOM ONLY

MASTER FIRE ALARM CONTROL PANEL
'FCP-A'

v2-2

v2-1        n2-1

15cd         15cd         30cd         30cd         75cd 1/8W         1/8W         1/8W         1/8W         1/2W

v2-2        v2-4        v2-5        v2-6
n2-2        n2-3        n2-4        n2-5       v2-7

15cd         15cd	K 1/4W         1/8W

BUILDING E

(1)FW

120V DEDICATED CIRCUIT (PROVIDE RED HANDLE C.B. W/ LOCK-ON

DEVICE & LABEL PER NFPA 72 SECTION 10.6.5.2, 10.6.5.4.)

WP	75cd (2)A	2W	1W

(1)A (TYP.)

75cd         30cd         15cd         75cd         WP 1/8W         1/8W         1/8W         1/2W         4W

(2)C

120V DEDICATED CIRCUIT (PROVIDE RED HANDLE C.B. W/ LOCK-ON

DEVICE & LABEL PER NFPA 72 SECTION 10.6.5.2, 10.6.5.4.)

s1-1        s1-2        s1-3        s1-4        s1-5        s1-6        s1-7        s1-8        s1-9       s1-10

J

NETWORK FIRE ALARM CONTROL PANEL 'FCP-K'
(1)D H

v1-4

(1)B, (1)C (TYP.) WP (2)C           2W

v1-2        v1-3 v1-1        n1-1        n1-2

WP           30cd         75cd 2W            1/2W         1W

(1)A, (1)G (TYP.)

s1-1        s1-2        s1-3

v1-6        v1-7        v1-8	(1)FW v1-5        n1-3        n1-4        n1-5        v1-9

WP           15cd         15cd         75cd         WP 1W            1/8W         1/8W         1W            2W

(2)C        (2)C

s1-4        s1-5        s1-6        s1-7        s1-8        s1-9       s1-10

HC-K3

s1-17      s1-16      s1-15      s1-14      s1-13      s1-12      s1-11

HC-K4

s1-20      s1-19      s1-18      s1-17      s1-16      s1-15      s1-14	s1-11

ERV-1 s1-25

(1)D	(1)A, (1)G (TYP.)	(1)A (TYP.) s2-1        s2-2        s2-3        s2-4        s2-5        s2-6        s2-7        s2-8        s2-9       s2-10

HC-A2

s2-15      s2-14      s2-13      s2-12      s2-11

HC-A1

(1)DW

NETWORK FIRE ALARM CONTROL PANEL
'FCP-E'

J

(1)B, (1)C (TYP.)

v1-2        v1-3        v1-4        v1-5        v1-6        v1-7	v1-8        v1-9 v1-1        n1-1        n1-2        n1-3        n1-4        n1-5        n1-6        n1-7        n1-8        n1-9

WP           30cd         30cd         15cd         75cd         15cd         15cd         15cd         15cd         15cd 2W            1/4W         1/4W         1/8W         1W            1/8W         1/8W                         1/2W         1/8W

v2-1	v2-2        v2-3	v2-4        v2-5        v2-6        v2-7        v2-8

n2-1        n2-2        n2-3        n2-4        n2-5        n2-6        n2-7        n2-8        n2-9        n2-10	H

15cd         15cd         75cd         15cd         15cd         15cd         75cd         75cd         15cd         15cd 1/4W                         1W            1/2W                         1/4W         1W            1W            1/8W         1/8W

v2-18      v2-17      v2-16      v2-15      v2-14      v2-13      v2-12      v2-11      v2-10      v2-9 n2-20     n2-19     n2-18     n2-17     n2-16     n2-15     n2-14     n2-13     n2-12     n2-11

(1)DW	15cd         30cd         75cd 1/4W         1/2W         1W

30cd         75cd 1/4W         1W

30cd         15cd         15cd         15cd         15cd 1/2W         1/8W         1/8W         1/4W         1/8W

G

BUILDING C

BUILDING D

(1)FW

120V DEDICATED CIRCUIT (PROVIDE RED HANDLE C.B. W/ LOCK-ON DEVICE & LABEL PER NFPA 72 SECTION 10.6.5.2, 10.6.5.4.)

v1-7	v1-12

v2-19

n2-21      v2-20	G

15cd         WP 1/8W         2W

(2)C

(1)A, (1)G (TYP.)

s1-1        s1-2        s1-3        s1-4        s1-5        s1-6        s1-7        s1-8        s1-9       s1-10

120V DEDICATED CIRCUIT (PROVIDE RED HANDLE C.B. W/ LOCK-ON F	DEVICE & LABEL PER NFPA 72 SECTION 10.6.5.2, 10.6.5.4.)

v1-5

(1)B, (1)C (TYP.)	(2)C

v1-1        v1-3        v1-4        v1-5 n1-1        n1-2        n1-3        n1-4

WP 4W

v1-6        v1-8        v1-9 n1-5        n1-6        n1-7

WP (2)C	2W

v1-10	v1-11

n1-8        n1-9        n1-10

HC-E3

s1-20      s1-19      s1-18      s1-17      s1-16      s1-15      s1-14      s1-13      s1-12      s1-11

HC-E1	HC-E2

s1-23	(1)A (TYP.)

General Notes	F

E

NETWORK FIRE ALARM CONTROL PANEL 'FCP-C'

D

(1)B, (1)C (TYP.)                  WP (2)C           4W

v1-1        v1-2        v1-3        v1-4        v1-6        v1-7                       v1-8        v1-9 n1-1        n1-2        n1-3        n1-4        n1-5        n1-6        n1-7        n1-8        n1-9

30cd         30cd         75cd         75cd         15cd         15cd         15cd         75cd         75cd 1/4W         1/2W         1W            1W            1/2W         1/2W                         1W            1W

v2-7

WP (2)C	2W

v2-2        v2-3        v2-4        v2-5        v2-6        v2-8	v2-9        v2-9 v2-1        n2-1        n2-2        n2-3        n2-4        n2-5        n2-6        n2-7        n2-8        n2-9

WP           15cd         30cd         15cd         75cd         75cd         15cd         15cd         75cd         75cd 4W            1/8W         1/4W         1/2W         1W            1W            1/2W                         1W            1W

(1)A, (1)G (TYP.)

s1-1        s1-2        s1-3        s1-4        s1-5        s1-6        s1-7        s1-8        s1-9       s1-10

HC-C5        HC-C6

s1-20      s1-19      s1-18      s1-17      s1-16      s1-15      s1-14      s1-13      s1-12      s1-11

NETWORK FIRE ALARM CONTROL PANEL
'FCP-D'

75cd         75cd         75cd 1W            1W            1W

(2)C v1-2

WP 4W

v2-3

WP (2)C	4W

v2-1        v2-2        v2-4 n2-1        n2-2        n2-3

75cd         75cd         75cd 1W            1W            1W

30cd         75cd         75cd         30cd         30cd         15cd         75cd 1/2W         1W            1W            1/2W         1/2W                         1W

v1-13 n1-11

75cd 1W

v2-5	v2-6        v2-7

n2-4        n2-5        n2-6       n2-7        n2-8        n2-9        n2-10

15cd         15cd         15cd         15cd         30cd         15cd         15cd 1/4W	1/4W         1/4W

v2-15      v2-14      v2-12      v2-11      v2-9        v2-8

n2-17     n2-16     n2-15     n2-14     n2-13     n2-12     n2-11

30cd         30cd         15cd         15cd         15cd         15cd         15cd 1/2W         1/2W         1/8W         1/8W         1/8W         1/4W

(2)C	(2)C

v2-13	v2-10

s2-1        s2-2        s2-3        s2-4        s2-5        s2-6        s2-7        s2-8        s2-9       s2-10

(1)D	s2-20      s2-19      s2-18      s2-17      s2-16      s2-15      s2-14      s2-13      s2-12      s2-11

(1)A (TYP.) s2-21      s2-22      s2-23      s2-24      s2-25      s2-26      s2-27      s2-28      s2-29      s2-29A

HOOD SUPPR. SYS.
s2-35      s2-34      s2-33	s2-30

HC-E4	MUA-1 (1)DW

R
Hardin-Davidson Engineering	E17850 356 Pollasky Ave., Suite 200, Clovis, CA 93612
559.323.4995 tel ● 559.323.4928 fax
www.hardin-davidson.com	Consultant

McKinley/Fowler Elementary School Clovis Unified School District
Fresno, CA 93727

Fire Alarm System Single Line Diagram
Drawing

E

D

(1)D	HC-C7        HC-C8	(1)A

s2-1

C

s2-2        s2-3        s2-4        s2-5        s2-6        s2-7        s2-8        s2-9       s2-10

HC-C9	HC-C3        HC-C4

s2-19      s2-18      s2-17      s2-16      s2-15      s2-14      s2-13      s2-12      s2-11

(1)A, (1)G (TYP.)

s1-1        s1-2        s1-3        s1-4

WP                            WP 4W                            2W
. 23724
No. C37102	C

s1-5        s1-6        s1-7        s1-8        s1-9       s1-10

HC-C1                           HC-C2 (1)A (TYP.)
(1)DW

HC-D5	HC-D6

s1-20      s1-19      s1-18      s1-17      s1-16      s1-15      s1-14      s1-13      s1-12      s1-11

-D2	HC-D1	HC-D7 1-23      s1-24      s1-25      s1-26      s1-27      s1-28      s1-29

(1)D	HC-D3	(1)A	HC-D4        (1)A (TYP.)

Architect

No.	Revision/Submission

3	Addendum 3- Electrical Rebid

Date

03/28/23

B	s2-1        s2-2        s2-3        s2-4        s2-5        s2-6        s2-7        s2-8        s2-9       s2-10	B

HC-D8	HC-D9	HC-D10

s2-20      s2-19      s2-18      s2-17      s2-16      s2-15      s2-14      s2-13      s2-12      s2-11

s2-21      s2-22      s2-23      s2-24      s2-25      s2-26

(1)DW

Revision

Designed By:      SD Copyright 2022 Darden Architects

A 	 Scale:	As indicated Drawn By:	HDE

A1	Fire Alarm System Single Line Diagram	Project Number:     2116 Checked By:       SD

No Scale	Date:	09/19/2022 Reviewed By:     SD

X/E502	A

Sheet: 	         of: 	

1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17	18	19		20 AD3- EX04