APPLICABLE CODES

·	2022 CALIFORNIA ADMINISTRATIVE CODE - CCR TITLE 24, PART 1
·	2019 CALIFORNIA BUILDING CODE - CCR TITLE 24, PART 2
·	2019 CALIFORNIA ELECTRICAL CODE - CCR TITLE 24, PART 3 ·	2019 CALIFORNIA MECHANICAL CODE - CCR TITLE 24, PART 4 ·	2019 CALIFORNIA PLUMBING CODE - CCR TITLE 24, PART 5
·	2019 CALIFORNIA ENERGY CODE - CCR TITLE 24, PART 6 ·	2019 CALIFORNIA FIRE CODE - CCR TITLE 24, PART 9
·       2019 EXISTING BUILDING CODE - CCR TITLE 24, PART 10 ·       2019 CALIFORNIA GREEN CODE - CCR TITLE 24 PART 11
·	2019 CALIFORNIA REFERENCE CODE - CCR TITLE 24 PART 12 ·       TITLE 19 CCR PUBLIC SAFTEY, STATE FIRE MARSHALL
REGULATIONS
·	 2019 NFPA 72 FOR FIRE ALARM SYSTEM. CFC CH 33 FIRE SAFTEY DURING CONSTRUCTION AND DEMOLITION

	
P

	

				

J

BUILDING ANALYSIS

OCCUPANCY:	A3, B EXISTING AREA:	690 FT2
CONSTRUCTION TYPE:	TYPE III - 1HR. - SPRINKLERED
FLOOD HAZARD ZONE X (SHADED):
AS DELINEATED ON THE FEDERAL EMERGENCY MANAGEMENT AGENCY'S FLOOD INSURANCE RATE MAP (MAP NUMBER 06019C1580H) FOR COMMUNITY NO. 060044, CITY OF CLOVIS, FRESNO COUNTY, CALIFORNIA, EFFECTIVE FEBRUARY 18, 2009, THE PROPERTY SHOWN ON THIS MAP LIES FULLY WITHIN FLOOD ZONE AREA DESIGNATED ZONE X (SHADED), WHICH ARE AREAS OF 0.2% ANNUAL CHANCE FLOODING.
	
SCOPE OF WORK
	
THE SCOPE OF WORK IS AS INDICATED BY THE CONTRACT DRAWINGS AND SPECIFICATION AND IS SUMMARIZED AS
FOLLOWS:
· REPLACE EXISTING WALK-IN COOLER & FREEZER. SPACE IS STAFF ONLY AND DOES NOT INVOLVE ANY STUDENT
PARTICIPATION NOR ARE THEY AVAILABLE TO THE GENERAL PUBLIC.
· REPLACE EXISTING REFRIGERATION CONDENSING UNITS ON ROOF.
	
SHEET INDEX
	
MECHANICAL
	SHEET COUNT
	
G-1	COVER SHEET
M-1	MECHANICAL DEMOLITION FLOOR & ROOF PLAN
M-2	MECHANICAL FLOOR & ROOF PLAN
M-3	MECHANICAL SCHEDULES & DETAILS
M-4	MECHANICAL SPECIFICATIONS
	1 2
3
4
5
	
ELECTRICAL
		
E1.01      SYMBOLS LEGEND, NOTES, ABBREVIATIONS
E1.02      ADDITIONAL ELECTRICAL NOTES
E1.03      PARTIAL SINGLE LINE DIAGRAM, PANEL SCHEDULE, WEIGHT AND DIMENSION SCHEDULE
E2.01      ELECTRICAL SITE PLAN
E3.01      PARTIAL BUILDING 'K' DEMOLITION ELECTRICAL ROOF & FLOOR PLAN
E3.02      PARTIAL BUILDING 'K' ELECTRICAL ROOF & FLOOR PLAN
E4.01      TYPICAL DETAILS
	6
7 8

9 10

11

12
	
STRUCTURAL
		
S1.0	STRUCTURAL DETAILS
	13
	
SHEET COUNT TOTAL:
	13
	
APPROVALS:

APPLICATION # 02-120017

DSA
IDENTIFICATION STAMP DIV. OF THE STATE ARCHITECT

APP:02-120017 INC: REVIEWED FOR

FLS	ACS
✔	✔
SS ✔            DIVISION OF THE STATE ARCHITECT D E P A R T M E N T O F G E N E R A L S E R V I C E S

DATE:	03/01/2023	

R
No. M34846 Exp. 6-30-24

A

DATE:	12-27-2022

GENERAL NOTES:

1.      ALL WORK SHALL CONFORM TO 2019 EDITION TITLE 24, CALIFORNIA CODE OF REGULATIONS (CCR).

2.     CHANGE TO THE APPROVED DRAWINGS AND SPECIFICATIONS SHALL BE MADE BY ADDENDA OR CONSTRUCTION CHANGE DOCUMENT (CCD) APPROVED BY DSA, AS REQUIRED BY SECTION 4-338, PART 1, TITLE 24, CCR.

3.      A "DSA CERTIFIED" PROJECT INSPECTOR EMPLOYED BY THE DISTRICT (OWNER) AND APPROVED BY DSA SHALL PROVIDE CONTINUOUS INSPECTION OF THE WORK. THE DUTIES OF THE INSPECTOR ARE DEFINED IN SECTION
4-342, PART 1, TITLE 24, CCR. PROJECT REQUIRES A CLASS 3 INSPECTOR.

4.     A DSA ACCEPTED TESTING LABORATORY DIRECTLY EMPLOYED BY THE DISTRICT (OWNER) SHALL CONDUCT ALL THE REQUIRED TESTS AND INSPECTIONS FOR THE PROJECT.

5.     THE INTENT OF THESE DRAWINGS AND SPECIFICATIONS IS THAT THE WORK OF THE ALTERATION, REHABILITATION OR RECONSTRUCTION IS TO BE IN ACCORDANCE WITH TITLE 24, CCR. SHOULD ANY EXISTING CONDITIONS SUCH AS DETERIORATION OR NON-COMPLYING CONSTRUCTION BE DISCOVERED WHICH IS NOT COVERED BY THE CONTRACT DOCUMENTS WHEREIN THE FINISHED WORK WILL NOT COMPLY WITH TITLE 24, CCR, A CONSTRUCTION CHANGE DOCUMENT (CCD), OR A SEPARATE SET OF PLANS AND SPECIFICATIONS, DETAILING AND SPECIFING THE REQUIRED WORK SHALL SUBMITTED TO AND APPROVED BY DSA BEFORE PROCEEDING WITH THE WORK. (SECTION 4-317(C), PART 1, TITLE 24, CCR)

6.     LAYOUT OF MATERIALS, EQUIPMENT AND SYSTEMS IS GENERALLY DIAGRAMMATIC UNLESS SPECIFICALLY DIMENSIONED. SOME WORK MAY BE SHOWN OFFSET FOR CLARITY. THE ACTUAL LOCATIONS OF ALL MATERIALS, PIPING, DUCTWORK, FIXTURES, EQUIPMENT, SUPPORTS, ETC. SHALL BE CAREFULLY PLANNED, PRIOR TO INSTALLATION OF ANY WORK TO AVOID ALL INTERFERENCE WITH EACH OTHER, OR WITH STRUCTURAL, ELECTRICAL, ARCHITECTURAL, OR OTHER ELEMENTS. ALL DUCT AND PIPE OFFSET ELBOWS FOR COORDINATION BETWEEN TRADES ARE NOT SHOWN. CONTRACTOR SHALL INCLUDE SUFFICIENT FUNDS FOR THE COORDINATION OFFSETS IN THE BID. VERIFY THE PROPER VOLTAGE AND PHASE OF ALL EQUIPMENT WITH THE ELECTRICAL PLANS. ALL CONFLICTS SHALL BE CALLED TO THE ATTENTION OF THE ENGINEER PRIOR TO THE INSTALLATION OF ANY WORK OR THE ORDERING OF ANY EQUIPMENT.

7.     MEP COMPONENT ANCHORAGE NOTE
ALL MECHANICAL, PLUMBING, AND ELECTRICAL COMPONENTS SHALL BE ANCHORED AND INSTALLED PER THE DETAILS ON THE DSA APPROVED CONSTRUCTION DOCUMENTS. WHERE NO DETAIL IS INDICATED, THE FOLLOWING COMPONENTS SHALL BE ANCHORED OR BRACED TO MEET THE FORCE AND DISPLACEMENT REQUIREMENTS PRESCRIBED IN THE 2019 CBC, SECTIONS 1616A.1.18 THROUGH 1616A.1.26 AND ASCE 7-16 CHAPTER 13, 26 AND 30.

1. ALL PERMANENT EQUIPMENT AND COMPONENTS.

2. TEMPORARY OR MOVABLE EQUIPMENT THAT IS PERMANENTLY ATTACHED (e.g. HARD WIRED) TO THE BUILDING UTILITY SERVICES SUCH AS ELECTRICITY, GAS OR WATER.
3. MOVABLE EQUIPMENT WHICH IS STATIONED IN ONE PLACE FOR MORE THAN 8 HOURS AND HEAVIER THAN 400 POUNDS ARE REQUIRED TO BE ANCHORED WITH TEMPORARY ATTACHMENTS.

THE FOLLOWING MECHANICAL AND ELECTRICAL COMPONENTS SHALL BE POSITIVELY ATTACHED TO THE STRUCTURE, BUT THE ATTACHMENT NEED NOT BE DETAILED ON THE PLANS. THESE COMPONENTS SHALL HAVE FLEXIBLE CONNECTIONS PROVIDED BETWEEN THE COMPONENT AND ASSOCIATED DUCTWORK, PIPING, AND CONDUIT.

A.COMPONENTS WEIGHING LESS THAN 400 POUNDS AND HAVE A CENTER OF MASS LOCATED 4 FEET OR LESS ABOVE THE ADJACENT FLOOR OR ROOF LEVEL THAT DIRECTLY SUPPORT THE COMPONENT.
B.COMPONENTS WEIGHING LESS THAN 20 POUNDS, OR IN THE CASE OF DISTRIBUTED SYSTEMS, LESS THAN 5 POUNDS PER FOOT, WHICH ARE SUSPENDED FROM A ROOF OR FLOOR OR HUNG FROM A WALL.

FOR THOSE ELEMENTS THAT DO NOT REQUIRE DETAILS ON THE APPROVED DRAWINGS, THE INSTALLATION SHALL BE SUBJECT TO THE APPROVAL OF THE STRUCTURAL ENGINEER OF RECORD (SEOR) AND THE DSA DISTRICT STRUCTURAL ENGINEER. THE PROJECT INSPECTOR WILL VERIFY THAT ALL COMPONENTS AND EQUIPMENT HAVE BEEN ANCHORED IN ACCORDANCE WITH ABOVE REQUIREMENTS.

PIPING, DUCTWORK, AND ELECTRICAL DISTRIBUTION SYSTEM BRACING NOTE PIPING, DUCTWORK, AND ELECTRICAL DISTRIBUTION SYSTEMS SHALL BE BRACED TO COMPLY WITH THE FORCES AND DISPLACEMENTS PRESCRIBED IN ASCE 7-10 SECTION 13.3 AS DEFINED IN ASCE 7-10 SECTION 13.6.8, 13.6.7, 13.6.5.6, AND 2019 CBC, SECTIONS 1616A.1.23, 1616A.1.24, 1616A.1.25 AND 1616A.1.26.

THE METHOD OF SHOWING BRACING AND ATTACHMENTS TO THE STRUCTURE FOR THE IDENTIFIED DISTRIBUTION SYSTEM ARE AS NOTED BELOW. WHEN BRACING AND ATTACHMENTS ARE BASED ON A PREAPPROVED INSTALLATION GUIDE (E.G., OSHPD OPM), COPIES OF THE BRACING SYSTEM INSTALLATION GUIDE OR MANUAL SHALL BE AVAILABLE ON THE JOBSITE PRIOR TO THE START OF AND DURING THE HANGING AND BRACING OF THE DISTRIBUTION SYSTEMS. THE STRUCTURAL ENGINEER OF RECORD SHALL VERIFY THE ADEQUACY OF THE STRUCTURE TO SUPPORT THE HANGER AND BRACE LOADS.

1450 HERNDON AVE.

CONTACT: ADAM BELMONT

LAWRENCE ENGINEERING GROUP

BORELLI & ASSOCIATES, INC. 7084 NORTH MAPLE AVE. SUITE 101	2032 N. GATEWAY BLVD. FRESNO, CA 93720	FRESNO, CA 93727
(559) 431-0101	(559) 233-4438

CONTACT: RYAN CARLSON	CONTACT: JOHN BORELLI

U

V P8

P4	P7	A

P3            T     P9 P2                             P6
P1	P5	S

AREA OF WORK O	H

K

DSA APP#: 51096
02-115416

G	M2	B2

M2

N

OVERALL SITE PLAN SCALE: 1"=100'-0"

(E) PATH OF TRAVEL (POT).
“DESIGN PROFESSIONAL IN GENERAL RESPONSIBLE CHARGE STATEMENT: THE POT IDENTIFIED IN THESE CONSTRUCTION DOCUMENTS MEETS THE REQUIREMENTS OF THE CURRENT APPLICABLE CALIFORNIA BUILDING CODE (CBC) ACCESSIBILITY PROVISIONS FOR PATH OF TRAVEL REQUIREMENTS FOR ALTERATIONS, ADDITIONS AND STRUCTURAL REPAIRS. AS PART OF THE DESIGN OF THIS PROJECT, THE POT WAS EXAMINED AND ANY ELEMENTS, COMPONENTS OR PORTIONS OF THE POT THAT WERE DETERMINED TO BE NONCOMPLIANT WITH THE CBC HAVE BEEN IDENTIFIED AND THE CORRECTIVE WORK NECESSARY TO BRING THEM INTO COMPLIANCE HAS BEEN INCLUDED WITHIN THE SCOPE OF THIS PROJECT’S WORK THROUGH DETAILS, DRAWINGS AND SPECIFICATIONS INCORPORATED INTO THESE CONSTRUCTION DOCUMENTS. ANY NONCOMPLIANT ELEMENTS, COMPONENTS OR PORTIONS OF THE POT THAT WILL NOT BE CORRECTED BY THIS PROJECT BASED ON VALUATION THRESHOLD LIMITATIONS OR A FINDING OF UNREASONABLE HARDSHIP ARE INDICATED IN THESE CONSTRUCTION DOCUMENTS.
DURING CONSTRUCTION, IF POT ITEMS WITHIN THE SCOPE OF THE PROJECT REPRESENTED AS CBC COMPLIANT ARE FOUND TO BE NONCONFORMING BEYOND REASONABLE CONSTRUCTION TOLERANCES, THE ITEMS SHALL BE BROUGHT INTO COMPLIANCE WITH THE CBC AS A PART OF THIS PROJECT BY MEANS OF A CONSTRUCTION CHANGE DOCUMENT.”

PARRISH HANSEN 418 CLOVIS AVE. CLOVIS, CA 93612 (559) 323-1023

CONTACT: BOB PARRISH

A

E2	D	E1

C

F

Q

KEYNOTES: (THIS SHEET ONLY)

1     THIS PROJECT HAS NO DEFERRED SUBMITTALS.

Statement of General Conformance

FOR ARCHITECTS/ENGINEERS WHO UTILIZE PLANS, INCLUDING BUT NOT LIMITED TO SHOP DRAWINGS, PREPARED BY OTHER
LICENSED DESIGN PROFESSIONALS AND/OR CONSULTANTS

(Application No. _____________File No. ______________)

The Architectural, Structural and Electrical Drawings Listed above have been prepared by other design professionals or consultants who are licensed and/or authorized to prepare such drawings in this state. They have been examined by me for:

1) Design intent and appears to meet the appropriate requirements of Title 24, California Code of Regulations and the project specifications prepared by me, and
2) Coordination with my plans and specifications and is acceptable for incorporation into the construction of this project.

This Statement of General Conformance shall not be construed as relieving me of my rights, duties, and responsibilities under Section 17302 and 81138 of the Education Code and Sections 4-336, 4-341 and 4-344 of Title 24, Part 1. (Title 24, Part 1, Section 4-317 (b))

RYAN W. CARLSON
LICENSE NUMBER: M34846 EXPIRATION DATE: 6-30-24

4910 E. Clinton Way, Suite 101
(559) 431-0101
Fresno, CA 93727
FAX (559) 431-1362
E N G I N E E R I N G
G R O U P
REVISIONS
CLOVIS, CA 93619
1560 N. MINNEWAWA AVE.
--------------------------
COLD BOX REPLACEMENT
BUCHANAN HIGH SCHOOL
TITLE:

COVER

SHEET

SHEET:

MECHANICAL/PLUMBING PIPING/DUCTS/ELECTRICAL:

OPTION : SHALL COMPLY WITH THE APPLICABLE OSHPD PRE-APPROVAL MASON

WEST OPM #0043-13.	PROJECT	21191

/ / /
/
Fresno, CA 93727
FAX (559) 431-1362
G R O U P
REVISIONS
DSA
APPROVALS:

APPLICATION # 02-120017

(E) MECH UNIT TO REMAIN.

(E) MECH UNIT TO REMAIN.

(E) EXIT FAN TO REMAIN.

(E) ROOF ACCESS.

LEGEND
	
SYMBOL
	ITEM
	ABBR
	
	RL
		REFRIGERANT LIQUID
	RL

	RS
		REFRIGERANT SUCTION
	RS

	C
		CONDENSATE DRAIN
	CD

	FLEXIBLE CONNECTION
	FLEX

			REDUCER OR INCREASER

			POINT OF CONNECTION
	POC

db
					EXISTING (DESIGNATED)
	(E)

	NEW (DESIGNATED)
	(N)
	
	ABOVE GRADE
	AG
	
	BELOW GRADE
	BG

EMS
		ENERGY MANAGEMENT SYSTEM CONDUIT
	
EMS

T
	THERMOSTAT
	T'STAT

T
	EMS TEMP. SENSOR @ +4'-0" TOP OF BOX

IDENTIFICATION STAMP DIV. OF THE STATE ARCHITECT

APP:02-120017 INC: REVIEWED FOR

FLS	ACS
✔	✔
SS ✔            DIVISION OF THE STATE ARCHITECT D E P A R T M E N T O F G E N E R A L S E R V I C E S

DATE:	03/01/2023	

R
No. M34846 Exp. 6-30-24

A

DATE:	12-27-2022

/ / / /
/ / / /
/ /
/ /
/ / / /
/ / / /

(E) MECH UNIT TO REMAIN.

(E) MECH UNIT TO REMAIN.

(E) MECH UNIT TO REMAIN.

(E) CONDENSING UNITS TO BE REMOVED. TYP. OF 3. (E) PLATFORM TO REMAIN. SEE STRUCTURAL SHEET S1.0 FOR
(E) VTR.	ALTERATIONS.
/ / /	(E) VTR.

/ / /

(E) 1 HOUR OCCUPANCY SEPARATION

CLOVIS, CA 93619
1560 N. MINNEWAWA AVE.
--------------------------
COLD BOX REPLACEMENT
BUCHANAN HIGH SCHOOL
MECHANICAL DEMOLITION ROOF PLAN SCALE: 1/8"=1'-0"

FOOD VEST.	SERV.

K116	K120

	

TRANSFORMER

TRASH AREA

DISH WASH

K117

MECH.	STORAGE

K118	K119

KITCHEN

K121

WOMEN K131

PASSAGE K132

MEN	STAFF K130                                                                                                             K133

HALL K122

LOCKER JAN.	K125
K123

(E) FLOOR SINK

 / / / / / / / / / / / / / / / 

/
OFFICE

K126	COLD BOX

K127

/ / / / / / / / / 	 / / / / / / / / / / / / / / / / / / / / 

(E C
/ / /
/
/
/	FREEZER /  /                                                             K128

/
/
/ / / /

(E) FLOOR DRAIN

FOOD SERV.
K129

(E) FLOOR SINK

/ /
/ /
/ / / / / / / / / / / / / / / / / / / / / / /
/ / / / / / / / / / / / / / / / / / / / / / /
/ // // // //)// // // // // // / / / / / / / / / / / / /
/ /
/ /

/ / / /
	
/
	/

/
/
4910 E. Clinton Way, Suite 101
E N G I N E E R I N G
JAN.

/
/ / /
/ / /
(559) 431-0101
K124	/ / / /	(E)C

(E) FIRE SPRINKLER HEAD TO BE REMOVED AND REPLACED, TYP. OF 4 PER COOLER AND 4 PER FREEZER.

(E) EVAPORATOR & ASSOCIATED PIPING TO BE REMOVED. (TYP. OF 3)

(E) INSULATED PANEL TO BE REMOVED. TYPICAL OF FREEZER AND COOLER WALLS, FLOORS, AND CEILINGS.

MECHANICAL DEMOLITION FLOOR PLAN SCALE: 1/8"=1'-0"

TITLE:

MECHANICAL

DEMOLITION PLAN

SHEET:

PROJECT	21191

HALL
4910 E. Clinton Way, Suite 101
(559) 431-0101
Fresno, CA 93727
FAX (559) 431-1362
E N G I N E E R I N G
G R O U P
REVISIONS
DSA
APPROVALS:

APPLICATION # 02-120017

(E) MECH UNIT.

(E) 1 HOUR OCCUPANCY SEPARATION

IDENTIFICATION STAMP DIV. OF THE STATE ARCHITECT

APP:02-120017 INC: REVIEWED FOR

FLS	ACS
✔	✔
SS ✔            DIVISION OF THE STATE ARCHITECT D E P A R T M E N T O F G E N E R A L S E R V I C E S

DATE:	03/01/2023	

(E) MECH UNIT.

(E) MECH UNIT.

CU	(E) MECH UNIT.
	
	2
CU (N) CONDENSING UNIT ON PLATFORM. 3     SEE DET. B/M-3. (TYP. OF 3)

RELOCATED DEFROST TIMERS.

(E) VTR.
CU 1

(N) PLATFORM ON (E) PLATFORM. SEE SHEET S1.0 FOR PLATFORM FRAMING.

R
No. M34846 (E) MECH UNIT.	Exp. 6-30-24

A

DATE:	12-27-2022

(E) EXIT FAN.

(E) VTR.
(E) ROOF ACCESS.

CLOVIS, CA 93619
1560 N. MINNEWAWA AVE.
--------------------------
COLD BOX REPLACEMENT
BUCHANAN HIGH SCHOOL
MECHANICAL ROOF PLAN SCALE: 1/8"=1'-0"

FOOD VEST.	SERV.

K116	K120

	

TRANSFORMER

TRASH AREA

DISH WASH

K117

MECH.	STORAGE

K118	K119

KITCHEN

K121

WOMEN K131

PASSAGE K132

MEN	STAFF K130                                                                                                             K133

ROUTE (N) 3/4" CONDENSATE TO (E) FLOOR SINK. DISCHARGE
K122 THERETO WITH 1" MIN. AIR GAP.

LOCKER

JAN.	K125	OFFICE K123                                                                         K126

JAN.

K124

PROVIDE CLEANOUT AT ANGLES AND CHANGES OF DIRECTION OF CONDENSATE DRAIN PIPE, TYP.

(N) REFRIG. LIQUID AND REFRIG. SUCTION PIPING DN FROM CONDENSING UNITS ON ROOF. ROUTE ABOVE (N) BOX CEILING
7/8" RS &	PANELS.
1/2" RL	E
2                         FOOD SERV.
T
T	K129

1/2" RL. 2 SETS.
7/8" RS &	REFRIG. PIPING DOWN THRU BOX COLD                                                                                              CEILING PANEL. SEE DET. A/M-3. (TYP.)
BOX	FREEZER	T	ROUTE (N) 3/4" CONDENSATE TO K127                                                              K128                                                             (E) FLOOR SINK. DISCHARGE
THERETO WITH 1" MIN. AIR GAP.

COND. TRAP. SEE DET. D/M-3. (TYP.)

NOTES:

1. FREEZER BOX TO BE 17'-5"W x 23'-3"L x 8'-0"H, COOLER BOX TO BE 17'-5"W x 16'-6"L x 8'-0"H AND INCLUDE THE FOLLOWING:

STUCCO EMBOSSED 26 GA. GALV. INT. FINISH. SMOOTH CEILING FINISH.
22 GA. STAINLESS STEEL FLOOR. (x) LED LIGHT FIXTURES. DEFROST TIMER.
FREEZER PRESSURE RELIEF PORT.

2. COOLER DOOR TO BE 36" WIDE x 76" HIGH. FREEZER DOOR TO BE 36" WIDE x 76" HIGH.

E     (N) EVAPORATOR. 1     SEE DET. A/MP-2.
(TYP. OF 3)

BOTH DOORS TO HAVE:
E	DIAMOND PLATE ON LOWER 1/2 OF DOOR. 3                                                                                                                                                             VERTICAL ERGO HANDLE.

LED LIGHT & THERMOMETER SWITCH. FREEZER DOOR TO HAVE FRAME HEATER.

(N) FIRE SPRINKLER HEADS. TYP. OF 4 IN FREEZER AND 4 IN COOLER. SEE NOTE 5.

(N) COOLER AND FREEZER BOX. FOR WALL PANEL ATTACHMENTS, REFER TO 5/S1.0. FOR CEILING PANEL ATTACHMENT, REFER TO 4/S1.0.

3. SLOPE CD 1/4" PER FOOT DOWN INSIDE FREEZER BOX.

4. REFRIGERANT PIPING IS SHOWN AS A SINGLE LINE FOR CLARITY. EACH SINGLE REFRIGERANT LINE REPRESENTS 2 PIPES, REFRIGERANT LIQUID AND REFRIGERANT SUCTION, AS NOTED.

TITLE:

MECHANICAL

MECHANICAL FLOOR PLAN SCALE: 1/8"=1'-0"

5. EXISTING FIRE SPRINKLER SYSTEM TO REMAIN. REPLACE DRY SPRINKLER HEAD WITH NEW IN ACCORDANCE TO NPFA 13 (2016) §8.4.9. IF DRY SPRINKLERS ARE LESS THAN 10-YEARS OLD, HEADS MAY BE REPLACED IN ACCORDANCE TO NFPA 13 (2016) §6.2.1.1.1.

PLAN

SHEET:

PROJECT	21191

" M

							

AX.

							

						

Fresno, CA 93727
FAX (559) 431-1362
E N G I N E E R I N G
G R O U P
CLOVIS, CA 93619
1560 N. MINNEWAWA AVE.
--------------------------
COLD BOX REPLACEMENT
BUCHANAN HIGH SCHOOL
DSA
APPROVALS:

APPLICATION # 02-120017

EVAPORATOR SCHEDULE

DESIGNATION
	E 1
	E 2
	E 3
	
AIRFLOW (CFM)
	1,281
	1,371
	1,371
	
FLA (AMPS)
	1.0
	1.0
	1.0
	
MCA / MOCP
	10.1 / 15
	10.1 / 15
	10.1 / 15
	
VOLTS/PHASE
	208 / 1
	208 / 1
	208 / 1
	
NO. OF FANS
	2
	1
	1
	
TOTAL CAP. (MBH)
	14.60
	8.40
	8.40
	
AWEF (AT ARI)
	4.03
	4.03
	4.03
	
REFRIGERANT
	R-448A
	R-448A
	R-448A
	
EVAP. TEMP. (°F)
	25
	-20
	-20
	
BOX TEMP. (°F)
	35
	-10
	-10

REFRIGERANT PIPING
				
LIQUID (IN.)
	1/2
	1/2
	1/2
	
SUCTION (IN.)
	7/8
	5/8
	5/8
	
CONDENSATE CONN. (IN.)
	3/4
	3/4
	3/4
	
DIMENSIONS (IN.)
				
(LxWxH)
	75"x10"x27"
	75"x10"x27"
	75"x10"x27"

MANUFACTURER
	BOHN
	BOHN
	BOHN
	
MODEL NUMBER
	BEL0100BS6EMA
	BEL0080BS6EMAB
	BEL0080BS6EMAB
	
LOCATION
	COOLER
	FREEZER
	FREEZER
	
OPER. WT (LBS)
	60
	54
	54
	
ACCESSORIES
	1,3
	2,3
	2,3

1. PROVIDE WITH ELECTRIC DEFROST, 230V 1Ø 9.1 AMPS 2. PROVIDE WITH ELECTRIC DEFROST, 230V 1Ø 9.1 AMPS
3. PROVIDE WITH ELECTRONIC THERMOSTAT, THERMOSTATIC EXPANSION VALVE,

CONDENSING UNIT SCHEDULE

DESIGNATION
	CU 1
	CU 2
	CU 3
	
NAME PLATE AMPS
	13.3
	10.9
	10.9
	
VOLTS/PHASE
	208/1
	208/3
	208/3
	
MCA / MOP
	20 / 30
	20 / 45
	20 / 45
	
COMPRESSOR HP
	2.0
	3.0
	3.0
	
AWEF (AT ARI)
	7.6
	3.15
	3.15
	
COOLING CAP (MBH)
	14.6
	8.4
	8.4
	
AMBIENT (°F)
	110
	110
	110
	
REFRIGERANT
	R448A
	R448A
	R448A
	
SUCTION LINE CONN. (IN.)
	7/8
	5/8
	5/8
	
LIQUID LINE CONN. (IN.)
	1/2
	1/2
	1/2
	
DIMENSIONS (IN.)
				
(LxWxH)
	44"x30"x29"
	39"x28"x20"
	39"x28"x20"
	
MANUFACTURER
	BOHN
	BOHN
	BOHN
	
TYPE
	AIR-COOLED
	AIR-COOLED
	AIR-COOLED
	
SERVICE
	COOLER
	FREEZER
	FREEZER
	
MODEL NUMBER
	BCH0020MBALZA
	BCH0030LBACZA
	BCH0030LBACZA
	
LOCATION
	ROOF
	ROOF
	ROOF
	
OPER. WT (LBS)
	220
	297
	297
	
ACCESSORIES
	1,2
	1,2
	1,2

1. PROVIDE WITH ELECTRONIC THERMOSTAT

2. REPLACEABLE CORE SUCTION FILTER, REPLACEABLE CORE LIQUID FILTER, FAN CYCLING CONTROL, SUCTION ACCUMULATOR,

MANUAL RESET HIGH PRESSURE SWITCH.

7"	7"
SEE ENLARGED

VIEW BELOW.

PLAN VIEW

(N) CU UNIT
(297 LB. MAX)
(4) 1/4" LAG SCREWS (OR SIZE TO PROPER FIT MOUNT HOLES) x 3" MIN. EMBED TO WOOD.

(N) 22 GA. SHT. MTL. CAP SET OVER 30# FELT & 3/4" FIRE RETARDANT PLYWOOD.

(N) 3x6 JSTS.

(E) 2x6 JSTS.                                                                                    (N) PLATFORM ON TOP OF (E) PLATFORM. SEE SHEET S1.0.

(N) 3x6 BLKG. SEE DET. 3/S1.0.

CONDENSING UNIT ON PLATFORM	A SCALE: NONE                                                                                                                                                                   M-3

24" LONG P1000
OF BOLTS)
SEAL BOLT HOLES W/	UNISTRUT. (1 EA. PAIR URETHANE FOAM. (TYP.)

IDENTIFICATION STAMP DIV. OF THE STATE ARCHITECT

APP:02-120017 INC: REVIEWED FOR

FLS	ACS
✔	✔
SS ✔            DIVISION OF THE STATE ARCHITECT D E P A R T M E N T O F G E N E R A L S E R V I C E S

DATE:	03/01/2023	

R
No. M34846 Exp. 6-30-24

A

DATE:	12-27-2022

SOLENOID VALVE

20' MAX.

SLOPE DN. 1/4" PER 10 FT.

SEAL OPENING W/ URETHANE FOAM & COVER WITH ESCUTCHEONS (TYP.)

RL

RS

3/8"Ø BOLT THRU BOX. (TYP. OF 6)

EVAPORATOR

MAX. WEIGHT = 60 LBS.

RS RL

OIL TRAP RS

HOLD TO MIN.

NOTE:
IF LIFT IS HIGHER THAN 20' USE MULTIPLE TRAPS.

REFRIGERATOR OR	1-6" MIN.FREEZER BOX

CD. SLOPE DN. 1/4" PER FOOT MIN. INSUL. & WRAP W/ HEAT TAPE IN FREEZER BOX.

RS RISER DETAIL

SCALE: NONE

E                 EVAPORATOR MOUNTING DETAIL                                   B M-3               SCALE: NONE                                                                                                                                                                   M-3

#10 TEK SCREWS. (TYP. OF 4)

1 5/8"x1 5/8" x12GA STRUT.

24

(E) ROOFING.

NUT & WASHER, (TYP. AT TOP & BOTTOM OF MEMBER).

(E) METAL DECK

3/8"� ROD.

CONDENSING UNIT MAX. WEIGHT = 297 LBS.

PLATFORM. SEE DETAIL A/M-3

FINISH ROOF

REFRIGERANT PIPING. SEE PLAN FOR SIZE.

REVISIONS
3" MIN.

INSULATED PIPE (TYP.)

B-LINE 3690 STEEL J-HANGER FOR PIPE.

CONDENSING UNIT MOUNTING DETAIL

SCALE: NONE

C MM098	M-3

NOTES:

1. SEE PLANS FOR PIPE SIZE. MAXIMUM PIPE SIZE 7/8" NOT INCLUDING INSULATION.
2. MAXIMUM 6 FT SPACING AND AT EVERY CHANGE OF DIRECTION.

PIPE SUPPORT HANGER DETAIL

SCALE: NONE

F MP199	M-3

COVER OPENING W/ ESCUTCHEON ON EA. SIDE.

HAND-TIGHT PLUG.

CAPPED END FOR CLEANOUTS.

OPEN TOP OF CROSS FITTING

CONDENSATE DRAIN. SEE PLAN FOR SIZE AND CONTINUATION.

NEOPRENE HOSE. (SAME SIZE AS CONDENSATE DRAIN).

STAINLESS STEEL HOSE CLAMPS.

SEAL OPENING W/ URETHANE FOAM.

TO EVAP. COND. DRAIN.

FREEZER BOX

4" (MINIMUM).

4910 E. Clinton Way, Suite 101
(559) 431-0101
TITLE:

MECHANICAL

SCHEDULES &

CONDENSATE DRAIN CONNECTION DETAIL

SCALE: NONE

D P020	M-3

DETAILS

SHEET:

PROJECT	21191

CLOVIS, CA 93619
1560 N. MINNEWAWA AVE.
--------------------------
COLD BOX REPLACEMENT
BUCHANAN HIGH SCHOOL
APPROVALS:

APPLICATION # 02-120017

DSA
IDENTIFICATION STAMP DIV. OF THE STATE ARCHITECT

APP:02-120017 INC: REVIEWED FOR

FLS	ACS
✔	✔
SS ✔            DIVISION OF THE STATE ARCHITECT D E P A R T M E N T O F G E N E R A L S E R V I C E S

DATE:	03/01/2023	

MECHANICAL SPECIFICATIONS:	GENERAL MECHANICAL SPECIFICATIONS:

1.      GENERAL: ALL GENERAL MECHANICAL SPECIFICATIONS APPLY TO THIS SECTION.

2.      PIPE LAYOUT: ROUTE PIPING TO AVOID CUTTING STRUCTURAL MEMBERS. WHERE CUTTING OR NOTCHING IS REQUIRED, THE STRUCTURAL MEMBER SHALL BE REINFORCED IN ACCORDANCE WITH THE CALIFORNIA BUILDING CODE. PIPING SHALL BE INSTALLED TO ENSURE UNRESTRICTED FLOW. ELIMINATE AIR POCKETS, PREVENT UNUSUAL NOISE AND PERMIT COMPLETE DRAINAGE OF THE SYSTEM. PROVIDE INDIVIDUAL SHUT OFF VALVES AT EACH EQUIPMENT ITEM.

3.      PIPING MATERIALS:

1.	CODES AND REGULATIONS: ALL WORK AND MATERIALS SHALL BE IN ACCORDANCE WITH THE FOLLOWING CODES AS ADOPTED AND AMENDED BY THE AUTHORITY HAVING JURISDICTION. THE INTENT OF THE DRAWINGS AND SPECIFICATIONS IS TO CONSTRUCT THE FREEZER IN ACCORDANCE WITH THE 2019 EDITION OF TITLE 24, CALIFORNIA CODE OF REGULATIONS. SHOULD ANY CONDITIONS DEVELOP NOT COVERED BY THE CONTRACT DOCUMENTS WHEREIN THE FINISHED WORK WILL NOT COMPLY WITH SAID TITLE 24, CALIFORNIA CODE OF REGULATIONS. NOTHING IN THESE DRAWINGS OR SPECIFICATIONS IS TO BE CONSTRUED TO PERMIT WORK NOT CONFORMING TO THESE CODES.

R
No. M34846 Exp. 6-30-24

A

A.     REFRIGERANT

B.     CONDENSATE DRAIN

HARD DRAWN TYPE ACR COPPER. WROUGHT COPPER FITTINGS, SILVER ALLOY BRAZED, 1100°F, SILFOS.

HARD TEMPER TYPE L COPPER, ASTM B88, 95-5 TIN-ANTIMONY SOLDER, WROUGHT COPPER FITTINGS OR SCHEDULE 40 GALV. STEEL, ASTM A53. GALV. MALLEABLE IRON SCREWED FITTING, ANSI B16.3.

A.	CALIFORNIA BUILDING CODE - CBC - 2019

B.	CALIFORNIA MECHANICAL CODE - CMC - 2019 C.	CALIFORNIA PLUMBING CODE - CPC - 2019
D.	CALIFORNIA FIRE CODE - CFC - 2019

E.	CALIFORNIA ELECTRICAL CODE - CEC - 2019

F.                CALIFORNIA CODE OF REGULATIONS, TITLE 8, INDUSTRIAL RELATIONS G.               CALIFORNIA CODE OF REGULATIONS, TITLE 24, BUILDING STANDARDS
H.	NFPA 13, STANDARD FOR THE INSTALLATION OF SPRINKLER SYSTEMS, 2019

2.	 PERMIT CHARGES: OBTAIN ALL PERMITS REQUIRED FOR PERFORMING WORK AND PAY ALL RELATED FEES.

DATE:	12-27-2022

4.     VALVES AND FITTINGS:

A.     LINE VALVE: BRONZE BODY, BALL TYPE. TFE LOCKED IN SEALS. BACK SEATED VALVE STEM. CONTROLMATICS C-11.

B.     VIBRATION ISOLATING CONNECTION: SEAMLESS FLEXIBLE BRONZE TUBING, BRAID COVERED. SUITABLE FOR SYSTEM PRESSURE. AMERICAN.

C.     SOLENOID VALVE: FULL LINE SIZE. SPORLAN.

5.      PIPING FREEZE PROTECTION TAPE: THE SELF-REGULATING HEATING CABLE SHALL CONSIST OF TWO (2) 16 AWG NICKEL-COPPER BUS WIRES EMBEDDED IN PARALLEL IN A SELF-REGULATING POLYMER CORE THAT VARIES ITS POWER OUTPUT TO RESPOND TO TEMPERATURE ALL ALONG ITS LENGTH, ALLOWING THE HEATING CABLE TO BE CUT TO LENGTH IN THE FIELD. THE HEATING CABLE SHALL BE COVERED BY A RADIATION-CROSSLINKED, MODIFIED POLYOLEFIN DIELECTRIC JACKET. TO PROVIDE A GROUND PATH AND TO ENHANCE THE HEATING CABLE'S RUGGEDNESS, THE HEATING CABLE SHALL HAVE A BRAID OF TINNED COPPER AND AN OUTER JACKET OF MODIFIED POLYOLEFIN. POWER CONNECTION, END SEAL, SPLICE, AND TEE KIT COMPONENTS SHALL BE APPLIED IN THE FIELD. HEATING CABLE CIRCUIT SHALL BE PROTECTED BY A GROUND-FAULT DEVICE FOR EQUIPMENT PROTECTION. RAYCHEM XL-TRACE, OR EQUAL.

THE HEATING CABLE SHALL HAVE A SELF-REGULATING FACTOR OF AT LEAST 90 PERCENT. THE

SELF-REGULATION FACTOR IS DEFINED AS THE PERCENTAGE REDUCTION, WITHOUT THERMOSTATIC CONTROL, OF THE HEATING CABLE OUTPUT GOING FROM 40°F PIPE TEMPERATURE OPERATION TO 150°F PIPE TEMPERATURE OPERATION. THE HEATING CABLE SHALL OPERATE ON LINE VOLTAGES OF 120 VOLTS WITHOUT THE USE OF TRANSFORMERS. CABLE SHALL BE SIZED AS FOLLOWS:

MINIMUM PIPE SIZE	AMBIENT TEMPERATURE (INCHES)                                        0°F	-20°F_____ 3 OR LESS	5 WATTS	5 WATTS

ALL HEATING-CABLE COMPONENTS SHALL BE UL LISTED, CSA CERTIFIED, OR FM APPROVED FOR USE AS PART OF THE SYSTEM TO PROVIDE PIPE FREEZE PROTECTION. COMPONENT ENCLOSURES SHALL BE RATED NEMA 4X TO PREVENT WATER INGRESS AND CORROSION. INSTALLATION SHALL NOT REQUIRE THE INSTALLING CONTRACTOR TO CUT INTO THE HEATING-CABLE CORE TO EXPOSE THE BUS WIRES. CONNECTION SYSTEMS THAT REQUIRE THE INSTALLING CONTRACTOR TO STRIP THE BUS WIRES OR THAT US CRIMPS OR TERMINAL BLOCKS, SHALL NOT BE ACCEPTABLE. ALL COMPONENTS THAT MAKE AN ELECTRICAL CONNECTION SHALL BE REENTERABLE FOR SERVICING. NO COMPONENT SHALL USE SILICONE TO SEAL THE ELECTRICAL CONNECTIONS. AN EXCEPTION WILL BE MADE IN AREAS WHERE A CONDUIT TRANSITION IS REQUIRED.

THE SYSTEM SHALL BE CONTROLLED BY A LINE SENSING THERMOSTAT, (EC-TS) SET AT 40°F.

SYSTEM SHALL BE INSTALLED ON THE CONDENSATE DRAIN PIPING INSIDE THE WALK-IN REFRIGERATOR AND FREEZER BOXES. INSTALLATION SHALL BE PER MANUFACTURER'S RECOMMENDATIONS. APPLY THE HEATING CABLE LINEARLY ON THE PIPE AFTER PIPING HAS BEEN SUCCESSFULLY LEAK TESTED. SECURE THE HEATING CABLE TO PIPING WITH CABLE TIES OR FIBERGLASS TAPE. APPLY “ELECTRIC TRACED” LABELS TO THE OUTSIDE OF THE THERMAL INSULATION. AFTER INSTALLATION AND BEFORE AND AFTER INSTALLING THE THERMAL INSULATION, SUBJECT HEATING CABLE TO TESTING USING A 2500-VDC MEGGER, MINIMUM INSULATION RESISTANCE SHALL BE 20 MEGOHMS OR GREATER.

6.      PIPE INSULATION: RUBBER BASED ELASTOMERIC PREFORMED PIPE INSULATION. THERMAL CONDUCTIVITY SHALL NOT EXCEED 0.27 BTU-IN/HR-FT -°F AT A MEAN TEMPERATURE OF 70°F. REFRIG. PIPE 1/2" THICK, COND. DRAIN PIPE IN FREEZER 1" THICK. PROVIDE ADHESIVE BY SAME MANUFACTURER. ARMACELL ARMAFLEX. COVER INSUL. PIPE EXPOSED TO WEATHER WITH 0.024" STUCCO EMBOSSED ALUMINUM JACKET AND 0.016" THICK ALUM. FITTING CURVES.

7.      PIPE SUPPORT: TO 4" PIPE - STEEL "J" HANGER WITH SIDE BOLT; 5" AND LARGER PIPE - STEEL CLEVIS HANGER. LOAD AND JAM NUTS. SIZE AND MAX. LOAD PER MFGR'S. RECOMMENDATIONS. FELT LINER FOR COPPER PIPING. HANGER AND ROD SHALL HAVE GALV. FINISH. UNISTRUT.

8.     SYSTEM IDENTIFICATION: FOR PIPE SYSTEMS OTHER THE DRAIN, MARK FLUID CONVEYED IN PIPE AND DIRECTION OF FLOW. COLORS PER ANSI 13.1. LOCATE AT ENDS OF LINES, MAJOR CONNECTIONS, PENETRATIONS OF WALLS, FLOORS OR CEILING, 50' O.C. MAX. SPACING.

9.     CONTROLS:

3.	WORK BY OTHERS: UNLESS OTHERWISE NOTED, THE ELECTRICAL CONTRACTOR SHALL PROVIDE ALL POWER WIRING, MOTOR STARTERS IN MOTOR CONTROL CENTERS, DISCONNECTS AND CONDUIT.

4.	 GUARANTEE: THE CONTRACTOR SHALL REPAIR ANY DEFECTS DUE TO FAULTY MATERIALS OR WORKMANSHIP AND PAY FOR ANY DAMAGE TO OTHER WORK RESULTING THEREFROM WHICH APPEARS WITHIN A PERIOD OF ONE YEAR FROM DATE OF ACCEPTANCE OF WORK.

5.	EXAMINATION OF SITE: THE CONTRACTOR SHALL EXAMINE THE SITE PRIOR TO ORDERING OR FABRICATING ANY MATERIALS. EXISTING CONDITIONS THAT CONFLICT WITH THE CONSTRUCTION DOCUMENTS SHALL BE BROUGHT TO THE IMMEDIATE ATTENTION OF THE ENGINEER. NO ALLOWANCE SHALL BE MADE IN THE CONTRACTOR'S BEHALF FOR ANY EXTRA EXPENSE TO WHICH HE MAY BE PUT DUE TO FAILURE OR NEGLECT ON HIS PART TO MAKE SUCH AN EXAMINATION.

6.	 MATERIALS, EQUIPMENT AND INSTALLATION: EACH ITEM REFERRED TO ON THE DRAWINGS AND IN THE SPECIFICATIONS REPRESENTS THE STANDARD OF QUALITY DESIRED FOR MATERIALS, EQUIPMENT AND INSTALLATION. ALL SUBSTITUTIONS MUST BE REVIEWED IN WRITING BY THE ENGINEER. ALL MATERIALS AND EQUIPMENT SHALL BE NEW AND FREE FROM DEFECTS. ALL INSTALLATIONS SHALL BE AS RECOMMENDED BY THE MANUFACTURER AND AS SHOWN ON DRAWINGS.

7.	SUBMITTALS: WITHIN 30 DAYS OF CONTRACT AWARD, THE CONTRACTOR SHALL SUBMIT ELECTRONIC COPIES OF SHOP DRAWINGS FOR ALL MATERIALS, EQUIPMENT, ETC. PROPOSED FOR USE ON THIS PROJECT. SUBMITTALS SHALL BE A SINGLE FILE IN PDF FORMAT, WITH BOOKMARKS FOR TABLE OF CONTENTS AND EACH TAB, AND SUB-BOOKMARKS FOR EACH ITEM. MATERIAL OR EQUIPMENT SHALL NOT BE ORDERED OR INSTALLED UNTIL WRITTEN REVIEW IS PROCESSED BY THE ENGINEER. ANY ITEM OMITTED FROM THE SUBMITTAL SHALL BE PROVIDED AS SPECIFIED WITHOUT SUBSTITUTION.

8.	CLOSEOUT DOCUMENTS:

CONTRACTOR GUARANTEES: ALL CONTRACTORS INVOLVED IN THE PROJECT SHALL SUBMIT WRITTEN GUARANTEES FOR THEIR WORK FOR ONE YEAR FROM THE DATE OF ACCEPTANCE TO THE OWNER THROUGH THE ENGINEER.

RECORD DRAWINGS: CONTRACTORS SHALL OBTAIN A SET OF PROJECT PRINTS TO KEEP AT THE JOB SITE. CONTRACTORS SHALL MARK ALL CHANGES FROM DESIGN PLANS ON THE PRINTS. WORK UNDERGROUND SHALL SHOW DEPTH AND DISTANCE FROM NEARBY STRUCTURES. SUBMIT THE RECORD DRAWINGS TO THE ENGINEER FOR REVIEW.

OPERATING AND MAINTENANCE INSTRUCTIONS: TWO COPIES OF ALL EQUIPMENT
OPERATION AND MAINTENANCE INSTRUCTIONS AND WIRING DIAGRAMS SHALL BE FURNISHED TO THE OWNER, THROUGH THE ENGINEER..
Fresno, CA 93727
FAX (559) 431-1362
G R O U P
REVISIONS
O&M MANUAL SHALL INCLUDE COPIES OF ALL INSPECTION REPORTS & VERIFICATIONS REQUIRED BY THE ENFORCING AGENCY.

4910 E. Clinton Way, Suite 101
E N G I N E E R I N G
A.     REFRIGERATOR REFRIGERATION SYSTEM: REFRIGERATOR SYSTEM SHALL RUN ON INTERNAL CONTROLS AT THE CONDENSING UNIT AND THE THERMOSTATS AT THE REFRIGERATOR EVAPORATORS.

(559) 431-0101
B.     FREEZER REFRIGERATION SYSTEM: FREEZE SYSTEM SHALL OPERATE SIMILAR TO THE REFRIGERATOR SYSTEM.

C.     REFRIGERATOR SYSTEM ALARM MONITORING SYSTEM: THE REFRIGERATOR TEMPERATURE SET POINT SHALL BE 35°F (ADJ.).

E.     FREEZER SYSTEM ALARM MONITORING SYSTEM: THE FREEZER TEMPERATURE SET POINT SHALL BE 0°F(ADJ).

9.     TESTS: PERFORM ALL TESTS AS REQUIRED BY APPLICABLE CODES IN THE PRESENCE OF INSPECTOR.

TITLE: MECHANICAL
SPECIFICATIONS

SHEET:

PROJECT	21191

	D

			CO	ON  AT 
 O 	TI  
      ITC D     IC 
DOO 	  OO 
  A      

   
 I      T  I T	 A      O I AT	TO  CA 
 ATT TO	     DC 1      D A T C NO O       OTION  N O 
  2 
COND CTO      .  I      COND IT 	N C.
 
	NC TO  AN D TAI DIA     A 
 I      COND IT 	N C.
  	 I      	I     D. A O      	TO       C ANICA        I	NT  C     D     
 
COND IT   
CONN CTO     A N C  A      O A CO	T  AC      A   T      .
 AN  I      DI CONN CT       NA	AT  ATIN AND C C.
     C     TAC , D 	 IT      CI      OT CTION
     C     TAC , DO B     D     	 IT      CI      OT CTION
 O     IN 

 CONDA      ID DA IT  ON 
T BA C I IN  O T       OO      T	A      CONT O IN . I T       OO      IT T     
D 
 A B C
     C     TAC      IT ON      A           ITC     D CONT O      D,  	 OO BO  
       T	I ION 	BO .
 ATT TO	       C 211 DI	IN , 1       ITC 	 I      TIN CONT O	
D1
DSA

ARC FLASH WARNING LABEL REQUIREMENTS CONDITION 1

A C  A   A A D  A A D  A NIN  AB       A  B  I D  A	D      AC D ON A  N      AND      I TIN       CT ICA DI T IB TION BOA D ,  AIN       ITC BOA D ,
T AN O 	 ,  AN      ,  AN BOA D , DI CONN CT ,  CC . 	C C N C 11 .1 A
T AT I  IT IN T   CO     O T I   O  CT.  AB	     A     B A  I D TO      I TIN 
       I       NT 	  N	CONN CTION A       AD . T       AB	     A     	T T     
        I 	NT  O 11 .21 B        AN I      3 . 2 11       ID IN     B      IN        CTI     
CO O  ,   BO     O AN CO BINATION T	O .

CONDITION 2

A C  A   A A D  A NIN  AB	 O AN  NTI	 N	      CT ICA 	IC 
AND DI T IB TION       T      , T           C     TION TO 11 .1 B      A     B  TI I     D AND A           CT ICA CO      ON NT O T      DI T IB TION         I       NT      A      A      AN
A C  A   A NIN  AB      IT T       O O IN IN O      ATION 
a. NO INA    T	 O TA     
 . A C  A  BO NDA     
c.  INI A A C  ATIN O C OT IN 
 . AT  A T ON , B T NOT BOT O T       O  O IN  
INCID NT  N	 & CO	 ONDIN  O     IN DI TANC 
T      A C  A      	CAT     O     
T       AB	     A     	T T      	 I	NT  O 11 .21 B 	AN I      3 . 2 11
  ID IN     B      IN 	CTI      CO O , 	BO     O AN CO BINATION T	O .
T      CONT ACTO      A      A      T             I       NT  AN  ACT	  O ID T     
        I  D  AB  IN O OBTAIN T      	IC     O A T I D  A T O T        CT ICA 
 N IN      O   CO D.

CONDITION 3

A C  A   A A D  A NIN  AB	     A     B  I D  A	D  AC D ON A     N      
   IC        I	NT  IT T       O O IN IN O      ATION NO INA       T      
 O TA  , A AI AB      A     T C 	NT AT T            IC O	C	NT   OT CTI     
D     IC  , C A IN TI	O T      	IC O      C	NT   OT CTI      D  IC     BA D
ON T      A AI AB      A     T C 	NT AT T      	IC 	I       NT, T      DAT T     
 AB      A A      I D. T       AB	     A  	T T      	 I	NT  O 11 .21 B       
AN I      3 . 2 11   ID IN     B      IN        CTI      CO O , 	BO     O AN 
CO BINATION T 	O .

TYPICAL WALL DEVICE MOUNTING HEIGHTS ADA GUIDELINES

2   A .	2  2   A .

      
 A .	 A .

IN TA     ABO      CO NT     	IN TA     ABO      CO NT     
D     IC AT 	ABO     	D     IC AT    ABO     
 INI	D  OO .	 INI      D   OO .

   
 A 

1  
 A 

IN TA     D     IC AT 1 
ABO       INI	D  OO 

     ONT ACC      

  
 A .
  
3 	3 	 A .
 A .	 A .

1      A .	1  2   A .

IN TA     D     IC AT   	IN TA     D     IC AT  2 
ABO       INI	D  OO .	ABO       INI	D   OO .

 ID ACC      

A      O I AT      
CO	ON   AT 	     O AD      T D
 O  I NA 	 O  T     CT      
D     IC 

    A .
	 C  D	

1      IN.
	 C     D      

 OO 

 A     D     IC 	      ITC     DI	D     IC 

2      T      

  AN  I      	 AN  I      

D     IC T  	 O NTIN   I      T

      ITC	                                             NO  O  T AN    A. . . TO TO O D     IC 

DI	                                              NO  O  T AN    A. . . TO TO O D     IC 

     C  TAC  	NO 	T AN 1  A. . . TO BOTTO     O D     IC 

T . O T T  O IC 	NO 	T AN 1  A. . . TO BOTTO     O D     IC 

T . O T T  C A      OO	             NO  O  T AN    A. . . TO TO O D     IC 

DATA O T  T 	NO 	T AN 1  A. . . TO BOTTO     O D     IC 

INT  CO     O T  T 	NO 	T AN 1  A. . . TO BOTTO     O D     IC 

T       I ION O T  T 	NO 	T AN 1  A. . . TO BOTTO     O D     IC 

 IC O  ON O T  T 	NO 	T AN 1  A. . . TO BOTTO     O D     IC 

     C     TAC      , O T T ,       ITC	,  IT IN T       AC  AN        CI I D IN  CTION
 TC.  O NT D ABO      CO NT       11B 3      O T  CA I O NIA B I DIN COD .

C OC 	A      O N ON D A IN     

  A      	A      O N ON D A IN     

 AND D	                                      	TO A C IT CT     A   AN 

 AI D	                                        	TO A C IT CT     A   AN 

 A      CONC  	ABO             O      O  CTION INTO CO     IDO 
O  O  T AN   O A      O N ON D A IN 

     IT  I      T 	       D TAI  

     IT  A	                                      	D TAI  

	NC  I      TIN  A   AC  A      O N ON D A IN     

STANDARD SYMBOL LEGEND

 	 I T	D I NATO     INDICAT      I T       T  .	3  T IC  	TA      I           TA DANT 	OOD BAC BOA D,      O ID 
      ANTIT O 	OOD  	T TO  NCO      A      NTI       N T 
INDICAT D ON  AN .

 I T        IT        IN T 	NC BATT	BAC 	 NIT   	T ICA 	T	INA CABIN T  	AC O 	 O NT D  IT  A      
 I IN D TAI 	     TA DANT 	OOD BAC BOA D

3  I      T  I T	  A  O C I IN  O NT D.  3 INDICAT     CI C IT,  a 	 AN BOA D  	AC O 	 O NT D a INDICAT       ITC CONT O .
     IT  I      T C I IN O  A      O NT D, A     O	INDICAT     DI     CTION.	DI T IB TION O       ITC BOA D
N     T A  IN 

     I TIN  O      I      TIN 
 1	 ATT TO	       C 1 1 ON O  , 1       ITC 	 I      TIN CONT O      	T AN O	

 2	 ATT TO	       C 1 2 ON O  , 2       ITC 	 I      TIN CONT O      	T	T AN O	

	 D DI CONN CT   OTO  AT D. 	NI      D AND IN TA      D B 
      CT ICA CONT ACTO . DI CONN CT TO B 	NI      D  IT D A 
D2	 ATT TO	       C 212 DI	IN , 2       ITC 	 I      TIN CONT O	                          	NT             I     D ACCO DIN TO NA	 AT DATA ON        I	NT
D3	 ATT TO	       C 213 DI	IN , 3       ITC 	 I      TIN CONT O	                          IN TA  D.  I      A    A  A	 ATIN O DI CONN CT,  B   O      ,  C 
 O DI CONN CT 	I	NT . I NO A	 ATIN I INDICAT D ON
 AN  I      DI CONN CT       NA	AT  ATIN AND C C.
 ATT TO	     D  1  D A T C NO O      OCC     ANC   N O 	 N      D DI CONN CT   OTO  AT D,       NI	D AND IN TA      D B 
      a	 ATT TO	            1 1       ITC ,  a INDICAT           ITC 	CONT O . 2	      CT ICA CONT ACTO  1  A	 ATIN O DI CONN CT,  2  
 TT	N     T TO  AC OT	 IT O T A CO	A INDICAT     1   ITC 	       A B      O	          I     D. A O 	TO       C ANICA        I	NT  C     D	 O 
D a	 ATT TO	     D     1 1 DI	,  a INDICAT           ITC 	CONT O . 2	DI CONN CT            I           NT . I NO A	 ATIN I INDICAT D ON

 TT	N     T TO  AC OT	 IT O T A CO	A INDICAT     1   ITC 	                      A N TIC  OTO  TA T      	NI      D, IN TA      D AND CONN CT D B 
 	 ATT TO	                   OTO N O 	      CT ICA CONT ACTO  N       OT           I  NOT D.

 2	 ATT TO	          2 1      C     TAC     CONT O	                                                                 OTO        NI      D AND IN TA      D B       C ANICA CONT ACTO AND
 AN     ID NTI ICATION	CONN CT D B       CT ICA CONT ACTO .

CI C IT ID NTI ICATION	        T     
      ITC	ID NTI ICATION
 I            IN        AD. 	TO OT	DI CI IN  AN .
 N      a	INT	ION A A	DOO CONTACT      O I ION,   T ICA D TAI .

 I      TIN AND      C     TAC      OO     CONT O	     A     B  OCAT D ABO      T  	 	INT	ION A A	       AD

CONT O      D D     IC      A A  A D C I IN T     N  OCAT T       OO     CONT O	                       INT	ION A A	 OTION D T CTO , AI     A INDICAT D ON  AN . AT T  N A      T AD AC NT  OO      IT A T BA C I IN . I NO T BA C I IN                                          O ND
     I T  OCAT T   OO     CONT O	IN T            CT ICA  OO .  AB     A      OO 
 I      TIN AND      C     TAC     CONT O	 IT T       OO     NA      ,  OO     N      B     ,	CI C IT B     A      
AND CI C IT     T      CONT O .	     I TIN ABO           O ND COND IT

  IT O      I A      ID DA IT  ON 	     I TIN  ND 	O ND COND IT

 I	O D 	      I     D A C ANN     I O      AC  A .      O ID A 
ACC      O I ,  ITTIN     , DI ID      ,  TC  O A CO	T AND 	
a	  T TO	 A           ITC  2 A, 12  2   ,  a INDICAT     CONT O 	     NCTIONA   T      .

OC         OCC  ANC  N O CO BO  A       ITC  2 A, 12  2    AT D	 I	O D  AC  A 	TICA      N .      O ID A      BO      ,  ITTIN     , AND

       	C I IN O  A      O NT D   NCTION BO 	N	      CT ICA 	I	NT
      BO     I      AND N      B      A INDICAT D

     C     TAC , D 	 2 A, 12  &      O ND	     I TIN       CT ICA 	I	NT TO       AIN

     C     TAC , D 	C I IN  O NT D	     I TIN       CT ICA 	I	NT TO B D      O I	D

     C     TAC , D 	  IT ON      A           ITC  D CONT O      D	     O ND  I       IT 	 N IN      ATION  I      	N. .C.,  .O.N.

COND IT CONC A D IN  A     O C I IN     .      O ID N      B  O  I  
N     T A      O  AC      A      I       I           A     B D T	IN D B OC D
            C     TAC , D	  IT      CI   OT CTION IN       AT 	OO 	N C      A      O B ANC CI C IT,.  ITC 	,  TC.      O ID   A AT 
CONN CT D TO T           A     COND CTO     AND  O TA      D O 
 	2 A, 12       C     TAC , D	  IT T O      B  O T 	CON ID     ATION . A     COND IT   A      A       O ND COND CTO   .

     C     TAC , DO B     D     	  2 2 A, 12  &      O ND	COND IT CONC A D  ND	O ND O B  O      OO ,  INI            I  I 
     C     TAC , DO B     D     	C I IN  O NT D	3  .      O ID N      B  O  I	N C  A      O B ANC CI C IT,       ITC 
	,  TC.   O ID       A AT N     T A      O  AC      A   I     .  I        A 
B D T	IN D B OC D CONN CT D TO T           A     COND CTO     AND
     C     TAC , DO B     D     	  IT ON      A           ITC     D CONT O      D	 O TA      D O CON ID  ATION . A     COND IT      A      A           O ND

     C     TAC , DO B     D     	  IT ON      A           ITC     D CONT O      D,
 	 OO BO  CA	T  AT 	          I     D.
     C     TAC ,   CIA  	TO   OO   AN  O      C     TAC      I     .	COND IT DO N
 	 	T NOT N      B        ,        NOT D C I TION ON  A	         T. T	ON O T T      O ID & IN TA     2 AN BO  IT 1 COND IT.
 	     N     A NOT N      B        , 	NOT D C I TION ON  A	         T.
 T B       INTO T BA C I IN .  O  A D C I IN     ,      N T      COND IT TO T  CAB     T        INATION  OCATION INDICAT D         T       I       DIA     A .

DATA O T T   O ID & IN TA  2 AN BO  IT 1 COND IT.  T B      	 
INTO T BA C I IN .  O  A D C I IN     ,      N T      COND IT TO T      CAB 

	 

T	INATION  OCATION INDICAT D        T       I	DIA     A .	D I NAT      I      AND       ANTIT O 	D	       	D       C     D	
     C     TAC ,  	 OO BO  CA	T  AT 	          I     D.		     O ID AND IN TA     T O  A      T	CONN CTO     AND T  AC      AT . T  T               O ID AND IN TA     	COA IA CAB          O      AC CONN CTO TO
CA      T   AT  	          I     D.	T      CAB     T      AD ND & T       INAT  IT A  A      T	CONN CTO .

T	 ON O T T,  	 OO BO  CA	T  AT 	          I     D.	T 	T	I ION O T T IN 	 OO BO  CA	T  AT 	      	I  D,

DATA O T T,  	  OO BO  CA      T   AT  	          I     D.	  	N      B      IN  A     NT	I INDICAT       ANTIT O D  IC . T ICA  O 
INT     CO     O T T,  	 OO BO  CA	T  AT 	          I     D.	A     T	O D     IC  .

	     ,  OO  O NT D D     	     C     TAC , DATA  AC , AND	      A         A     O C I IN  O NT D,            TO  I       DIA     A     AND O 
T	ON  AC .	NOT     ON  AN .

DATA O T T, C I IN  O NT D	C	TI	C OC  O  A     IN 	         

C I IN O  A      O NT D  I	ACC	 OINT   O I ION .      O ID 	C 	CO BINATION C OC &       A      ,        C OC &       A       	BO .
AND IN TA     ON DATA CAB          O      AC ACC	 OINT TO ID .  O 
 A D C I IN      T	INAT T      CAB	INTO A BO  IT CO	 AT .
 O T BA C I IN      T	INAT T  CAB	INTO A C B CAT  O T AND
C	  T      CAB      IT 1 	T O  AC .  A      ABO      T      T BA 
C I IN .      O ID A  AB     B N AT T      T BA C I IN TO INDICAT DATA
 O T ABO     .

ELECTRICAL EQUIPMENT NOTES

1.      T            CT ICA D A IN      A      DIA     A	ATIC AND INDICAT T           N     A 
A     AN	NT O   CT ICA 	I	NT, D  IC     AND  I IN . 	TO T      T C NICA       CI ICATION  O        T	         I	NT .

ELECTRICAL SHEET LIST
 1. 1        BO     	ND, NOT     , ABB	IATION , AND
        I	NT 

 1. 2 ADDITIONA       CT ICA NOT 

 1. 3  A TIA  IN	DIA     A ,  AN      C     D	,       I      T AND
DI      N ION  C     D	

 2. 1       CT ICA  IT  AN

 3. 1  A TIA B I DIN   D      O ITION       CT ICA  OO &
 OO  AN

 3. 2  A TIA B I DIN         CT ICA  OO &  OO  AN

     . 1 T ICA D TAI 

T	  AN A  ACCO      ANI D  IT BOO       CI ICATION T AT
 O       A T O T      CONT ACT DOC	NT .

ABBREVIATIONS

A, A      	A	
A.C.	ABO  CO NT     
A. . .	ABO   INI      D  OO 
A 	A	IN	COND CTO O B     
BD	BOA D
C                     COND IT CAB                CABIN T
CAT 	CAB     T	I ION
CB	CI C IT B     A	
CC	C NT      TO C NT     
C T	CI C IT
CO	COND IT ON     	T COND IT  IT 	 I     
C B	CO	NICATION 	BO 
C 	CO	COND CTO O B     
DB	DI T IB TION  AN 
     	     I TIN 
      	               NC 
      T	      CT IC       TA IC T BIN 
 .O. .	 ND O     IN 
     O	               NC  O       O 
      C	      CT IC  AT      COO      
 	        
 .A. A	 I      A A      
 AC 	 I      A A	CONT O  AN 
 .B.O.	       NI      D B OT	NI	D B O N     
 A	           OAD A	
      C	         IB           TA IC COND IT
 	 O       ITC 
 	          N      O ND  I     
     CI	     O ND  A     T CI C IT INT	     T
 ND	     O ND
	                  A     ANI  D  I ID  T      
 C	 O I ONTA C O  CONN CT
 ID	 I	INT N IT DI C A	
	                  I	                  ODI      
I.B.O.	IN TA      D B OT	
I.B. .	IN TA      D AND CONN CT D B       CT ICA 
CONT ACTO 
ID 	INT	DIAT DI T IB TION      A	 DATA 
I 	I O AT D      O ND
INT	INT      ION A A      
     B	     NCTION BO 
     	 I O O T 
     A	 I O O T  A	 
      	 I O ATT
	C	 I      IDTI      T 	IB           TA IC COND IT
 C 	 I      TIN CONT O  AN 
 T 	 I      TIN 
     	 O      O TA     
 TD	 O NT D
 T 	 O NTIN 
     O	 AIN 	ON 
N	N     T A 
 N 	N      
N 	NI      T  I      T
N.I.C.	NOT IN CONT ACT
N.T. .	NOT TO  CA 
O.C. OC	ON C NT     
O OI	O N      	NI      D O N      IN TA      D
 	     A 
 	 O 
 .A. A	     B IC ADD         T      
 B	          BO 
 I 	 O T INDICATO  A	
 N 	 AN 
 B	 O       	BO 
     C  C     T.      C     TAC 
	.	         I	ATO 
      O	      OCATAB     B I DIN       O TAB     B I DIN 
      	 OO 
 	 A ID  TA T
     	 AC  NIT
 C 	 I NA C          NT 	AND       AN 
 . .	 C     IT  I      T
 CTB	 I NA AND CO	NICATION T      INA BAC BOA D
 B	 I NA 	BO 
 D	              	 ION D     IC 
 TB	 I NA T      INA BOA D
 TC	 I NA T      INA CABIN T
      	      ITC 
T B	T	ON 	BO 
T 	TA	      ITC 
T 	T	ON 
T	              T      INA 
T 	T ICA 
TTB	T	ON T      INA BOA D TTC	T	ON T      INA CABIN T
 .C.	 ND      CO NT     
      	 ND	O ND
 .O.N.	 N       OT	I  NOT D
 	 O T      O TA     
 . .	 ANDA      OO 
 	 ATT 
      	      AT	OO 
	                 I       O D

APPROVALS: APPLICATION #

IDENTIFICATION STAMP DIV. OF THE STATE ARCHITECT

APP:02-120017 INC: REVIEWED FOR

FLS	ACS
✔	✔
SS ✔            DIVISION OF THE STATE ARCHITECT D E P A R T M E N T O F G E N E R A L S E R V I C E S

DATE:	03/01/2023	

R
No. M34846 Exp. 6-30-24

A

7084 N. Maple Ave., Suite 101
(559) 431-0101
Fresno, CA 93720
FAX (559) 431-1362
E N G I N E E R I N G
G R O U P
REVISIONS
CLOVIS, CA 93619
1560 N. MINNEWAWA AVE.
--------------------------
COLD BOX REPLACEMENT
BUCHANAN HIGH SCHOOL
DATE:	12-27-2022

	AD 	NO  O  T AN    A. . . TO TO O D     IC 

 I	O D	 O NTIN      I      T      A     B      C T AT T     
 O	T D     IC  O NT D ON  I	O D I 
AT 1  A. . . TO BOTTO     O D     IC ,  .O.N.

NOT     
1.      A     	TICA       A	        NT A       ABO       INI      D  OO   A. . . . 2.     	D A IN       O NON T ICA  O NTIN      I      T .
3.      	 O NTIN      I      T A  NOT      O N, 	      TO A C IT CT  A  AN .
 .          C     TAC      ,  I      T       ITC	, T       ON DATA O T T AND OT      
     C	D   CT ICA D     IC     T AT A           O N BAC TO BAC ON  A      
      A ATIN CO     IDO ,  OO      AND O     N A     A      A     B       A AT D
 O I ONTA  B AT   A T 2 INC	. T I 	I	NT I TO  ATI  BOT 
T      CONDITION AT  I       AT D CO     IDO  AND  O ND T AN  I ION  ACTO 
B T	N A  CO     IDO  ,  OO      AND O     N A     A INC     DIN      T     IO 
 A  .

CO  I      T 2 22 B BO	I AND A OCIAT , INC. A      I      T 	D T       I	O BO	I AND A OCIAT , INC. AND IT      B IDIA     CO      ANI 
                  IT CO       ON  A     CO      I      T AND OT       A  ICAB          O      T  I      T IN T           AN . T         AN A      NOT TO B          OD C D, C AN     D, O CO I D IN AN  O       O  ANN             AT O         , NO A      T        TO B A  I N D TO A T I D  A T  IT O T  I T OBTAININ T            ITT N           I  ION AND CON NT O BO          I AND A OCIAT , INC. AND IT      B IDIA     CO      ANI . IN T             NT O AN  NA T O I     D              O T         AN B A T I D
 A T , T      T I D  A T      A      O D T       I	O BO	I AND A OCIAT , INC. AND IT      B IDIA     CO      ANI      A	     AND   A     B A T      CO T O 
BO	 I AND A  OCIAT , INC. AND IT      B IDIA     CO      ANI     	A  	A OCIAT D  IT D	NDIN AND  N O CIN T	  I      T .

TITLE:

SYMBOLS LEGEND, NOTES, 

ABBREVIATIONS

SHEET: E1.01

		

Borrelli
Cons ltin 
2 32 N.  a
 resno, CA.
     one 	
 tt	
ca ai      or BAI 22111
					
c.

&
 lec
te 
 3
 23 . o
relli
	
Associates, In trical  n ineers
a Bo le ar 
 2 
3 13 
rrellien ineerin .co     
en ineerin .co 

PROJECT	21191

	cational Clo is     D B c anan i      c ool Col Bo e lace ent 22111 1 1.	, 12 3 2 22 3 3	      ,  2 32, A toCAD  D  i	      alit  rint . c3, A C  ll  lee D  3 .	 2 .	Inc es 

CLOVIS, CA 93619
1560 N. MINNEWAWA AVE.
--------------------------
COLD BOX REPLACEMENT
BUCHANAN HIGH SCHOOL
DSA

GENERAL NOTES

1.      A      O      AND  AT     IA      A     CON O	TO  AT T COD     AND O DINANC . IT I T     
INT NTION O T	   AN AND   CI ICATION TO CO	A     T IN                 I     D TO
     O ID CO	T AND O      ATI            T	. T      CONT ACTO      A     	NI       ABO ,
 AT     IA , T AN O TATION, 	I       NT,  I C      AN O   	IC ,  TC. 	I     D TO ACCO	I      T I 	T. AN T IN 	IC  A B      A ONAB     CON T      D A A
N C  A      A T O T      IN TA ATION      A     B INC     D D. NOT IN IN T           AN O 
  CI ICATION  A B CON T	D TO 	IT  O      NOT CON O      IN TO AN 
CON T     CTION COD .

2.     A     	I	NT      A      A      T TIN  ABO ATO      AB     ATTAC     D  . . C. .A.  TC. A 
	N. .C. 11 .      OO O T TIN  AB	          I     D  IT A       B ITTA . T     
CONT ACTO      A     B 	ON IB      O A     T	 	I	NT . T      CONT ACTO 
     A     NOTI  T      A C IT CT N IN	  IO TO       C A IN , I AN O T            CI I D
 AT     IA  AI D T	          I	NT .  	A  I D C  TI I D      OD CT  A B 
	I     D  O  I D A	B D CO      ON NT,      O ID C  TI I D 	O T B AN
A  O     D T TIN A     NC ACC     TAB     TO T      A T O ITI   A IN       I DICTION. INC     D A     T TIN 	IN BID.

3.     T       N IN	IN 	IC A       I IT D TO  	A ATION O  AN AND       CI ICATION .
T       AN AND       CI ICATION A      INT ND D TO B 	D A CON T     CTION       ID IN 
ON     AND NOT T  TOTA IN T	NT O CONT ACT DOC	NT . IT I NOT T     
INT NTION O AN CON T     CTION   AN TO DI ID  O      A ON DI	NT T AD  .
	I   CO     O  O       IT      N     A CONT ACTO O N       INC T       N IN	I NOT
	       I IN T       OB. T       N IN	 I          O ID INT	TATION O T     
CON T     CTION DOC       NT , B T  	I ION I  ND      T             ON IBI IT O T     
O N      O  I A OINT     .

 .      O     IN C A ANC   A     B  AINTAIN D A 	C. .C N. .C.  O A      AN       , 	IC 
	I	NT, DI CONN CT       ITC ,  TC.  OCA  TI IT CO      AN  O     IN C A ANC 
	I	NT      A     A O B OB	D.  O	        I	NT  AN     ACT	     OD CT
 A  A     IN DI      N ION. T      CONT ACTO      A     B       ON IB      O COO DINATION O  O     IN C A ANC           I          NT          N  A IN O T T            CT ICA        I        NT.

 .     A AI AB      A     T C	NT      A     B  INDICAT D ON A     N	IN TA      D  	IC 
		I	NT. T       I D  A     IN      A     INC     D T      DAT O T       A     T C	NT CA C     ATION  A  	O	D.

 .     T      CONT ACTO      A     	I          ACT  OCATION O T	INA BO	AND COND IT
 NT ANC     O A     	I	NT A AIN T      O D A IN      B     O       T BBIN       COND IT 
O   N T ATIN      T     IO  A	O B I DIN	.

 .     IN CA     O INT	NC B T	N       CT ICA 	I	NT      O N ON T      D A IN     
AND OT	        I	NT, T      CONT ACTO      A     NOTI  T       N IN      IN       ITIN 
B     O           OC     DIN .

MEP ANCHORAGE BRACING NOTE

	CO      ON NT ANC O A      NOT 

A           C ANICA , 	BIN , AND       CT ICA CO      ON NT   A     B ANC O  D AND
IN TA      D 	T      D TAI     ON T      D A A	O  D CON T     CTION DOC	NT . 	 NO D TAI I INDICAT D, T       O O IN CO      ON NT   A     B ANC O  D O B AC D TO
	T T       O C AND DI  AC	NT
	I	NT       C IB D IN T      2 1 CBC  CTION 1 1 A.1.1 T     O	1 1 A.1.2 AND
A C  1 C A T	13, 2 , AND 3 

1. A     	AN NT 	I	NT AND CO      ON NT .
2. T	O A     ,  O AB     O  OBI     	I	NT T AT I 	 AN NT 
ATTAC     D  . .  A D  I  D TO T  B I DIN  TI IT        IC          C A 
  CT ICIT ,  A O 	 AT     .  	 AN NT     ATTAC     D   A     INC     D A 
  CT ICA CONN CTION      C     T 	 O 11 22  O T      C     TAC	 A IN A
	IB     CAB .
3. T	O A      O AB     O  OBI            I	NT 	IC I      A I      T AN 	              O ND 
O  A A C NT      O  A   OCAT D  	T ABO  T      AD AC NT  OO O 	 OO 
	 T AT DI  CT     	O T T  CO      ON NT I  	I     D TO B   T AIN D IN A
 ANN      A	O  D B D A.

T       O O IN       C ANICA AND       CT ICA CO      ON NT      A     B  O ITI	
ATTAC     D TO T       T  CT      B T N     D NOT D      ON T AT D I N CO	IANC  IT T  
	NC  NOT D ABO     . T	 CO      ON NT   A      A  	IB     CONN CTION 
     O ID D B T      N T      CO      ON NT AND A OCIAT D D CT O  ,  I IN , AND COND IT.
	IB     CONN CTION 	T A O      O 	NT IN BOT T AN         AND  ON IT DINA 
DI     CTION  

A. CO      ON NT       I      IN        T AN 	 O ND AND  A  A C NT      O 	 A  
 OCAT D        T O        ABO      T      AD AC NT  OO O  OO 	     T AT DI     CT 
 	O T T      CO      ON NT.
B. CO      ON NT       I      IN        T AN 2  O ND , O IN T      CA     O 
DI T IB T D   T	, 	T AN   O ND 	 OOT, 	IC A  	ND D      O     A
 OO O  OO O       N      O     A  A .

T      ANC O A      O A           C ANICA ,       CT ICA AND 	BIN CO      ON NT   A     B 
     B  CT TO T      A	O A O T      D I N      O       IONA IN      N     A    ON IB     C A      
O  T     CT     A  N IN	D	AT D    ON IBI IT AND ACC     TANC B D A. T     
     O  CT IN      CTO  I           I     T AT A     CO      ON NT AND 	I	NT  A  B     N ANC O     D IN ACCO DANC  IT T      AABO  	I 	NT .

APPROVALS: APPLICATION #

IDENTIFICATION STAMP DIV. OF THE STATE ARCHITECT

APP:02-120017 INC: REVIEWED FOR

FLS	ACS
✔	✔
SS ✔            DIVISION OF THE STATE ARCHITECT D E P A R T M E N T O F G E N E R A L S E R V I C E S

DATE:	03/01/2023	

R
No. M34846 Exp. 6-30-24

A

DATE:	12-27-2022

 .     A     O TDOO D     IC          A     B       AT 	 OO .

 .     ON      A O  	BO	A           O N. CONT ACTO      A          O ID ADDITIONA 	
BO      	T      A      	I     D TO  A      A  O     AB     IN TA ATION. A     	BO      
ABO           O ND      A     B  AD  OC AB . A               BO       ND 	O ND      A      A     
 O D DO N BO T AND B T A  IC  AT D.

1 .  A      A      AN	 IT  A ANOID TA     .   O ID T            ITT N  AN   C     D	AT A 
 AN      .

11. A       OO	O ND  O NT D 	I	NT      A      IT ON A CONC     T  AD 3  I	
T AN 	O NDIN           AC  O INT     IO 	I	NT AND       O      T     IO 
	I	NT.

12. CONT ACTO      A     	NI      A   AT     IA , TOO ,  ABO ,        I	NT AND 	I ION N C  A     TO CO         T IN TA ATION, C  C O T AND INITIA O       ATION.

13. CONT ACTO      A     	I  A     DI      N ION AND      N     A A     AN	NT O        I	NT
     O N AND      A          B IT      O D A IN       O A     	I	NT      IO TO 	C A .

1 . CA TION      O     D B 	D 	N      CA ATIN O T     NC IN TO  OCAT   I TIN 
 ND	O ND COND IT . COO DINAT  IT A     NCI          C A  ND	O ND
	IC A      T      IO TO      CA ATION.

1 . T      CONT ACTO      A     B 	ON IB      O  A IN  I IT D T       IT AND  ATI  I D
 I	A TO T  CONDITION  ND      	IC T   O      I TO B 	O	D. T     
CONT ACTO      A     C  C A     O T      CONDITION 	IC  A A      CT  I  O     . T     
 IT  I IT   A     B  AD   IO TO      B ITTIN T      BID. BIDD	  A     	A     AN      A  IT 
 I IT  IT T      O N           O CT  N IN	.

1 . T      CONT ACTO      A     OBTAIN A 	 T O  AN 	N BIDDIN T       OB.

1 . A       A     COND CTO          A      A      T  I O N N     T A . NO   A IN O N     T A 
A O      D.

1 . A C     TI I D       CT ICA   A     B 	NT ON T           O  CT 	N	       CT ICA  O     
I IN   O	 . AN       CT ICA CONT ACTO I NOT 	T      O     T I            I           NT AND
     A     A O B C     TI I D I       I  O     IN A T             ON IB          O CT       CT ICIAN .
 IO ATION O T I 	I	NT B  IT	      CT ICIAN O  O     IN CONT ACTO 
     A     B 	O T D TO T       TAT  IC N  CONT ACTO BOA D A 	 I     D  ND  T     
     I TIN  ABO COD  CTION 1  .2. NO  O     NT	A      A O      D TO 	O	 O     
ON T I      O CT AND A     CIT IN	ANC 	I	NT 	T B       T      IO TO
	O      IN AN  O     .

1 . A     COND IT      A     B CONC A D  IT IN ATTIC  AC AND  A      .

2 . A          T     IO COND IT 	D ON T I   O CT      A     B I C O  I ID.

21. A      A T N	  D      A     B  TAIN	 T	     AD 31 .

22. A          T     IO      C     TAC           A     B      CI T	 IT A  OC IN ,       AT	OO IN  
CO	.

23. A     DI CONN CT      A     B      ADI     ACC      IB     AND IN  I      T O T             I	NT, 	T     
CA I O NIA       CT ICA COD . I T      DI CONN CTIN       AN CANNOT B  OCAT D
 IT IN  I      T O T      	I	NT 	D, IT      A      A      T      CA ABI IT O B IN 
 OC     D IN T      O     N  O ITION.

2 . A     COND CTO     IN  TA      D IN  ND	O ND O   T  OCATION      A     B  I T D  O 
      T  OCATION AND  A	D  IT        	C C.

2 .   IC     AND T	INA          A     B CO      	ION T  O   A	 	CO	, TIN
 AT D,  ON BA	 T	INA      IT T O O      AD AND IN      CTION  INDO      IT 
N      A D I IN , A  AN     ACT	D B B     ND T	 ,  A 2N O        A . C AN A 
	AC     AND IN TA      IT O ID IN IBITIN CO      O ND, B     ND      N T O	O 
	A . IN TA     CO	 ION CONN CTO      IT 3   CI C	     NTIA CO	 ION
D     , B     ND  	O 	A . T  IND NT      O OT       T	TOO      I     NOT B 
ACC     TAB .

2 . IN TA           C ANICA        A T N D        NO IC NA         AT  IT        IT  TT     IN ON B AC BAC      O ND ON A             I       NT, INC     DIN           BO      ,  IT D  C I TION
INDICAT D ON D A IN     . NA	AT          A          AD      ACT     A D C IB D ON T     
D A IN     . IN      N     A NA	AT  TT     IN  I           A     B 3 1 INC  I	 O A 
NA	 AT     	IN       D      AND B ANC CI C IT B     A      . ON  AIN 	IC  AN      
AND A  OT	NA	 AT      TT     IN      A     B 1  INC  I      .
2 .1      A           ITC BOA D ,       ITC	A ,  AN BOA D ,      D ,  OTO ,      NCTION BO      ,
          BO  , DI CONN CT       ITC  ,  TC.,      A     B  A	D TO INDICAT  AC 
D     IC O 	I       NT 	T   O	O I INAT     	C C 	. ,  I D ID NTI ICATION 	I     D,  B  O     C O              .

2 . COO DINAT 	I       NT  OCATION , CONT O AND  O	 I IN            I	NT AND CONN CT  OINT  IT A     A      ICAB     DI CI  IN .

2 .      O ID AND IN TA      	         NIT NA	AT DATA ON T             I	NT      O ID D.

2 .      IN TA       I TIN       CT ICA IN TA ATION DI T  B D. C     TAIN   I TIN       CT ICA 
IN TA ATION  A B  OCAT D IN  A , C I IN      O  OO     T AT A      TO B 	O     D
AND A      	NTIA  O T      O	ATION O OT	        AININ IN TA ATION . 	
T I CONDITION OCC	,      O ID A N	     T N ION O O I INA CI C IT ,  AC      A ,
	I	NT AND O T T TO      TAIN 	IC CONTIN IT . IN TA ATION   A     B 
CONC A D IN  INI      D A     A .

 I IN , D CT O     , AND       CT ICA DI T IB TION   T	B ACIN NOT 

 I IN , D CT O     , AND       CT ICA DI T IB TION   T	  A     B B AC D TO CO	
 IT T       O C     AND DI      AC	NT 	C IB D IN A C  1   CTION 13.3 A D     IN D IN A C  1  CTION13. . , 13. . , 13. . , 13. . AND 2 1 CBC,   CTION 1 1 A.1.2 , 1 1 A.1.2 , AND 1 1 A.1.2 .

T            T OD O   O IN B ACIN AND ATTAC	NT TO T       T     CT	 O T     
ID NTI I D DI T IB TION       T	A      A NOT D B O .   AT B ACIN AND ATTAC	NT 
A      BA  D ON A 	A	O     D IN TA ATION       ID  . ., O      D O	 O 2 13 CBC O 
 AT  , CO I  O T  B ACIN       T	IN TA ATION       ID O   AN A   A     B 
A AI AB     ON T       OB  IT      IO TO T       TA T O AND D     IN T       AN IN AND
B ACIN O T      DI T IB TION   T	. T       T     CT     A  N IN	O      CO D   A 
	I     T      AD       AC O T   T  CT      TO 	O T T       AN	AND B AC  OAD .

      C ANICA  I IN 	,       C ANICA D CT      D , 	BIN  I IN 	,       CT ICA 
DI T IB TION   T	      

	    D                 O TION 1 D TAI D ON T      A	O  D D A IN       IT 
     O CT       CI IC NOT     AND D TAI 

	    D                O TION 2      A     CO	 IT T      A      ICAB     O      D
7084 N. Maple Ave., Suite 101
(559) 431-0101
Fresno, CA 93720
FAX (559) 431-1362
E N G I N E E R I N G
G R O U P
REVISIONS
      A	O A  O	  O	2 13

TITLE:

		

Borrelli
Cons ltin 
2 32 N.  a
 resno, CA.
     one 	
 tt	
ca ai      or BAI 22111
					
c.

&
 lec
te 
 3
 23 . o
relli
	
Associates, In trical  n ineers
a Bo le ar 
 2 
3 13 
rrellien ineerin .co     
en ineerin .co 

ADDITIONAL ELECTRICAL      

NOTES

CO  I      T 2 22 B BO	I AND A OCIAT , INC. A      I      T 	D T       I	O BO	I AND A OCIAT , INC. AND IT      B IDIA     CO      ANI 
                  IT CO       ON  A     CO      I      T AND OT       A  ICAB          O      T  I      T IN T           AN . T         AN A      NOT TO B          OD C D, C AN     D, O CO I D IN AN  O       O  ANN             AT O         , NO A      T        TO B A  I N D TO A T I D  A T  IT O T  I T OBTAININ T            ITT N           I  ION AND CON NT O BO          I AND A OCIAT , INC. AND IT      B IDIA     CO      ANI . IN T             NT O AN  NA T O I     D              O T         AN B A T I D
 A T , T      T I D  A T      A      O D T       I	O BO	I AND A OCIAT , INC. AND IT      B IDIA     CO      ANI      A	     AND   A     B A T      CO T O 
BO	 I AND A  OCIAT , INC. AND IT      B IDIA     CO      ANI     	A  	A OCIAT D  IT D	NDIN AND  N O CIN T	  I      T .

SHEET: E1.02

PROJECT	21191

	cational Clo is     D B c anan i      c ool Col Bo e lace ent 22111 1 2.	, 12 3 2 22 3 3	      ,  2 32, A toCAD  D  i	      alit  rint . c3, A C  ll  lee D  3 .	 2 .	Inc es 

DSA
APPROVALS: APPLICATION #

MECHANICAL EQUIPMENT SCHEDULE

D I .

	
D C I TION
	
 A     CA 	
	 TA T      

 O T
	
  A 
	 A . OC D
 I     
	CON 
D IT
 I     
	COND CTO 
	
 ND.

	 I     
		
C  1
	COND N IN  NIT
	2  CA
		DI C.
	2     
	1
	NOT 2
	1 
	2
	NOT  
	NOT 3
	
C  2
																					
C 3
																			
 1
	     A O ATO  NIT
	1  A
																	
 2
																					
 3

NOT     
1.       T           A  AT D       ITC  O      ACTIONA  O	O	 OTO .
2.     	      TO T   AN      C     D	AND  IN       IN DIA  A      O T      CI C IT B     A      AND COND IT  I      , I NOT INDICAT D
 IT IN T       C     D	.
3.          O NDIN COND CTO  I  TO  ATC COND CTO  I     .
 .     	      TO CAB      I   C     D	 O T      COND CTO  I      .

     N     A NOT  
1.     COO DINAT  OCATION AND  O	 	I	NT  O   C ANICA        I	NT  IT       C ANICA CONT ACTO . 2.          O ID        D   ITC DI CONN CT         NA        AT  ATIN O       C ANICA  NIT  O O	OAD   OT CTION.

1

       N 
 	C 1

            D     

       N 
 	C 2
	
		PARTIAL SINGLE LINE DIAGRAM

			
		NOT TO  CA  

IDENTIFICATION STAMP DIV. OF THE STATE ARCHITECT

APP:02-120017 INC: REVIEWED FOR

FLS	ACS
✔	✔
SS ✔            DIVISION OF THE STATE ARCHITECT D E P A R T M E N T O F G E N E R A L S E R V I C E S

DATE:	03/01/2023	

R
No. M34846 Exp. 6-30-24

A

DATE:	12-27-2022

7084 N. Maple Ave., Suite 101
(559) 431-0101
Fresno, CA 93720
FAX (559) 431-1362
E N G I N E E R I N G
G R O U P
REVISIONS
CLOVIS, CA 93619
1560 N. MINNEWAWA AVE.
--------------------------
COLD BOX REPLACEMENT
BUCHANAN HIGH SCHOOL
TITLE:

		

Borrelli
Cons ltin 
2 32 N.  a
 resno, CA.
     one 	
 tt	
ca ai      or BAI 22111
					
c.

&
 lec
te 
 3
 23 . o
relli
	
Associates, In trical  n ineers
a Bo le ar 
 2 
3 13 
rrellien ineerin .co     
en ineerin .co 

PARTIAL SINGLE DIAGRAM, 

PANEL SCHEDULE, WEIGHT AND

DIMENSION SCHEDULE

CO  I      T 2 22 B BO	I AND A OCIAT , INC. A      I      T 	D T       I	O BO	I AND A OCIAT , INC. AND IT      B IDIA     CO      ANI 
                  IT CO       ON  A     CO      I      T AND OT       A  ICAB          O      T  I      T IN T           AN . T         AN A      NOT TO B          OD C D, C AN     D, O CO I D IN AN  O       O  ANN             AT O         , NO A      T        TO B A  I N D TO A T I D  A T  IT O T  I T OBTAININ T            ITT N           I  ION AND CON NT O BO          I AND A OCIAT , INC. AND IT      B IDIA     CO      ANI . IN T             NT O AN  NA T O I     D              O T         AN B A T I D
 A T , T      T I D  A T      A      O D T       I	O BO	I AND A OCIAT , INC. AND IT      B IDIA     CO      ANI      A	     AND   A     B A T      CO T O 
BO	 I AND A  OCIAT , INC. AND IT      B IDIA     CO      ANI     	A  	A OCIAT D  IT D	NDIN AND  N O CIN T	  I      T .

SHEET: E1.03

PROJECT	21191

	cational Clo is     D B c anan i      c ool Col Bo e lace ent 22111 1 3.	, 12 3 2 22 3 31	      ,  2 32, A toCAD  D  i	      alit  rint . c3, A C  ll  lee D  3 .	 2 .	Inc es 

R
DSA

      B D .  2 

					

					

			
	      B D .  

				

			

      B D .  2 

  B D .  1 

  B D .  B1 

      B D .  B2 

											

      B D .  C 

					

      B D .  2 

			

 B D .  

		

				

									

						

  B D .  

D .  2 

      B 

						

			

					

				
			
  B D .  

							

			

		

 
	 B D .   

 
		
3 
	
	 B D .   

 
		
2 
	
	 B D .   

 
		
1 

 B D .   

APPROVALS: APPLICATION #

WEST TEAGUE AVENUE

      B D .   

IDENTIFICATION STAMP DIV. OF THE STATE ARCHITECT

APP:02-120017 INC: REVIEWED FOR

FLS	ACS
✔	✔
SS ✔            DIVISION OF THE STATE ARCHITECT D E P A R T M E N T O F G E N E R A L S E R V I C E S

DATE:	03/01/2023	

      B D .   

  B D .  

      B D .  A1 

  B D .  A2 	      B D .  3 

No. M34846 Exp. 6-30-24

A

DATE:	12-27-2022

NORTH MINNEWAWA AVENUE
      B D .  

      B D .       

      B D .  1 
      B D .       

COLD BOX REPLACEMENT
  B D .  1 

BUCHANAN HIGH SCHOOL
      B D .  O 

      B D .  

CLOVIS, CA 93619
1560 N. MINNEWAWA AVE.
--------------------------
A	A O  O	

	      B D .  1 

      B D .  1 

  B D . N 

			
				
		      B D
	 .  
	1 

	      B D .  2 

				

Fresno, CA 93720
FAX (559) 431-1362
G R O U P
REVISIONS
1	ELECTRICAL SITE PLAN
 	 CA      1	

7084 N. Maple Ave., Suite 101
(559) 431-0101
E N G I N E E R I N G
TITLE:

		

Borrelli
Cons ltin 
2 32 N.  a
 resno, CA.
     one 	
 tt	
ca ai      or BAI 22111
					
c.

&
 lec
te 
 3
 23 . o
relli
	
Associates, In trical  n ineers
a Bo le ar 
 2 
3 13 
rrellien ineerin .co     
en ineerin .co 

ELECTRICAL SITE PLAN	

CO  I      T 2 22 B BO	I AND A OCIAT , INC. A      I      T 	D T       I	O BO	I AND A OCIAT , INC. AND IT      B IDIA     CO      ANI 
                  IT CO       ON  A     CO      I      T AND OT       A  ICAB          O      T  I      T IN T           AN . T         AN A      NOT TO B          OD C D, C AN     D, O CO I D IN AN  O       O  ANN             AT O         , NO A      T        TO B A  I N D TO A T I D  A T  IT O T  I T OBTAININ T            ITT N           I  ION AND CON NT O BO          I AND A OCIAT , INC. AND IT      B IDIA     CO      ANI . IN T             NT O AN  NA T O I     D              O T         AN B A T I D
 A T , T      T I D  A T      A      O D T       I	O BO	I AND A OCIAT , INC. AND IT      B IDIA     CO      ANI      A	     AND   A     B A T      CO T O 
BO	 I AND A  OCIAT , INC. AND IT      B IDIA     CO      ANI     	A  	A OCIAT D  IT D	NDIN AND  N O CIN T	  I      T .

SHEET: E2.01

PROJECT	21191

	cational Clo is     D B c anan i      c ool Col Bo e lace ent 22111 2 1.	, 12 3 2 22 3 31 3 	,  2 32, A toCAD  D  i	      alit  rint . c3, A C  ll  lee D  3 .	 2 .	Inc es 

CLOVIS, CA 93619
1560 N. MINNEWAWA AVE.
--------------------------
COLD BOX REPLACEMENT
BUCHANAN HIGH SCHOOL

	 OO     NA      
	TI	O   OO 
 AT O  
		
	 OO     NA      
      C ANICA  OO 
 TO A     
	
 1 1
 1 2
		 11 
 11 
		
 1 3
	 TO A     
	 12 
	 OOD        IC 
	
 1     
	 TO A     
	 121
	 ITC     N
	
 1     
	 TO A     
	 122
	 A	A 
	
 1     
	 ANITO   OO 
	 123
	 ANITO       OO 
	
 1     
	      N   T OO 
	 12 
	 ANITO            T OO 
	
 1     
		TIN  OO 
	 12 
	 OC	 OO 
	
 1     
	 TO A     
	 12 
	O IC 
	
 11 
	 T D NT  TO  
	 12 
	CO D BO 
	
 111
	O IC 
	 12 

 112
	  TIB	
	 12 
	 OOD        IC 
	
 113
	 A     T
	 13 
	      N       T OO 
	
 11 
	 O      N       T OO 
	 131
	 O      N       T OO 
	
 11 
	 OBB 
	 132
	 A A	A 
	
 11 
	  TIB	
	 133
	 TA      OO 
	
 11 
	DI   A   OO 

APPROVALS: APPLICATION #

	

1

DSA
ROOM SCHEDULE	 IDENTIFICATION STAMP DIV. OF THE STATE ARCHITECT

APP:02-120017 INC: REVIEWED FOR

FLS	ACS
✔	✔
SS ✔            DIVISION OF THE STATE ARCHITECT D E P A R T M E N T O F G E N E R A L S E R V I C E S

DATE:	03/01/2023	

R
No. M34846 Exp. 6-30-24

A

DATE:	12-27-2022

SHEET NOTES  

1	PARTIAL BUILDING 'K' DEMOLITION ELECTRICAL ROOF PLAN
 	 CA      1       1     

1.     CA 	DI CONN CT  O	TO      I TIN COND N IN  NIT .
	A     COND CTO  BAC TO  O     C AND        O       I TIN 
COND IT       TO ACC      IB      OINT AND CA O .      O ID AND
IN TA     A N	COND IT AND N	COND CTO  ,  	TO T  
      C ANICA  C  D	.   N COND IT AND COND CTO  TO N      
COND N IN  NIT  OCATION. CONN CT TO T       AN     AND
CI C IT INDICAT D ON  AN .  A      A     CONN CTION  O A
	     NCTIONIN   T      .

2.     CA 	DI CONN CT  O	TO      I TIN      A O ATO .      T ND
COND IT AND COND CTO     TO N	     A O ATO     A T     
IN TA ATION.  A      A     CONN CTION  O A 	     NCTIONIN 
  T      .

3.     CA 	DI CONN CT  I      T   ITC .      T ND CI C IT A 
 	I     D IN  I      ID TI      T 	IB           TA COND IT TO  OCATION O N        I      T   ITC A T      IN TA ATION O N	               .

 .     CA 	DI CONN CT T      T 	TI      C OC      OCAT D  I	ON
     ONT O      	      DOO AND  TO  IN A  A      AC .      T ND CI C IT AND   CONN CT A T      	AC	NT O      	     .

		 11 

		

 1

1 

 11 

									

							

 122

 12 

 123	 12 

 12 

 132

 121
 13 

       IN 

3	3	 

C C C

 	      T .

 	 12 	 12 

T .

2	2

 .

 .

 133

1.

2.

 12 

     O ID AND IN TA      BO ABO       I      T  I T	. INT     C     T
     I TIN CI C IT  O  I      T  I T          AND      T ND TO N	 I      T
 I T	 OCATION .      CONN CT TO CI C IT INDICAT D ON  AN .

CA 	DI CONN CT AND        O   O	TO      I TIN 
     A O ATO . 	A     COND CTO  BAC TO  O     C AND
       O       I TIN COND IT       TO ACC  IB      OINT AND CA O .
     O ID AND IN TA     A N	COND IT AND N	COND CTO  ,
 	TO T        C ANICA  C     D	. CONN CT TO N      
     A O ATO  OCATION IN ID COO      . CONN CT COND CTO  TO
T       AN     AND CI C IT INDICAT D ON  AN .  A      A 
CONN CTION  O A 	     NCTIONIN   T      .

GENERAL NOTES  

A     COND IT      N T ATION   A     B   A D  IT A	O  D
  A ANT TO 	 NT  OI T           N T ATION  IT IN T      	     
AND COO      .

REVISIONS
 I      A A        T	  A     B T T D AND IN      CT D IN ACCO DANC  IT N A  2, C A T      1 .

Fresno, CA 93720
FAX (559) 431-1362
G R O U P
2	PARTIAL BUILDING 'K' DEMOLITION ELECTRICAL FLOOR PLAN
 	 CA  1	1      

7084 N. Maple Ave., Suite 101
(559) 431-0101
E N G I N E E R I N G
TITLE:

		

Borrelli
Cons ltin 
2 32 N.  a
 resno, CA.
     one 	
 tt	
ca ai      or BAI 22111
					
c.

&
 lec
te 
 3
 23 . o
relli
	
Associates, In trical  n ineers
a Bo le ar 
 2 
3 13 
rrellien ineerin .co     
en ineerin .co 

PARTIAL BUILDING 'K'	

DEMOLITION ELECTRICAL

ROOF & FLOOR PLAN

CO  I      T 2 22 B BO	I AND A OCIAT , INC. A      I      T 	D T       I	O BO	I AND A OCIAT , INC. AND IT      B IDIA     CO      ANI 
                  IT CO       ON  A     CO      I      T AND OT       A  ICAB          O      T  I      T IN T           AN . T         AN A      NOT TO B          OD C D, C AN     D, O CO I D IN AN  O       O  ANN             AT O         , NO A      T        TO B A  I N D TO A T I D  A T  IT O T  I T OBTAININ T            ITT N           I  ION AND CON NT O BO          I AND A OCIAT , INC. AND IT      B IDIA     CO      ANI . IN T             NT O AN  NA T O I     D              O T         AN B A T I D
 A T , T      T I D  A T      A      O D T       I	O BO	I AND A OCIAT , INC. AND IT      B IDIA     CO      ANI      A	     AND   A     B A T      CO T O 
BO	 I AND A  OCIAT , INC. AND IT      B IDIA     CO      ANI     	A  	A OCIAT D  IT D	NDIN AND  N O CIN T	  I      T .

SHEET: E3.01

PROJECT	21191

	cational Clo is     D B c anan i      c ool Col Bo e lace ent 22111 3 1.	, 12 3 2 22 3 31	      ,  2 32, A toCAD  D  i	      alit  rint . c3, A C  ll  lee D  3 .	 2 .	Inc es 

REVISIONS

			

      	  1 

AN  O           

     B 	       

T A      A  A

T 

					

	
	 OO     NA      
	TI	O   OO 
 AT O  
		
	 OO     NA      
      C ANICA  OO 
 TO A     
	
 1 1
 1 2
		 11 
 11 
		
 1 3
	 TO A     
	 12 
	 OOD        IC 
	
 1     
	 TO A     
	 121
	 ITC     N
	
 1     
	 TO A     
	 122
	 A	A 
	
 1     
	 ANITO   OO 
	 123
	 ANITO       OO 
	
 1     
	      N   T OO 
	 12 
	 ANITO            T OO 
	
 1     
		TIN  OO 
	 12 
	 OC	 OO 
	
 1     
	 TO A     
	 12 
	O IC 
	
 11 
	 T D NT  TO  
	 12 
	CO D BO 
	
 111
	O IC 
	 12 

 112
	  TIB	
	 12 
	 OOD        IC 
	
 113
	 A     T
	 13 
	      N       T OO 
	
 11 
	 O      N       T OO 
	 131
	 O      N       T OO 
	
 11 
	 OBB 
	 132
	 A A	A 
	
 11 
	  TIB	
	 133
	 TA      OO 
	
 11 
	DI   A   OO 

APPROVALS: APPLICATION #

	

          C 2      ,     
 	C 2      , 2	 	C 2      ,     
C 
3
C 
1
2	             	C 2       

DSA
ROOM SCHEDULE	 IDENTIFICATION STAMP DIV. OF THE STATE ARCHITECT

APP:02-120017 INC: REVIEWED FOR

FLS	ACS
✔	✔
SS ✔            DIVISION OF THE STATE ARCHITECT D E P A R T M E N T O F G E N E R A L S E R V I C E S

DATE:	03/01/2023	

R
No. M34846 Exp. 6-30-24

A

DATE:	12-27-2022

 	 	 
 	 	 
SHEET NOTES  

1.          O ID AND IN TA     A 	INC      NCTION BO ,  O NT D
ABO      T       	      DOO  .      O ID AND IN TA     T O 1 1     INC 
C 
COND IT  O  O      O TA     .  O T COND IT ABO  C I IN 
	BAC TO DATA BO  OCAT D IN  OO      123. T      INAT AT BOT  ND .

2.          T ND CI C IT      O     T                IO                 O  D 	 COO      
  ITC	AND  A      CONN CTION TO T      N	  ITC  .  A     
COLD BOX REPLACEMENT
BUCHANAN HIGH SCHOOL
A      I      TIN CONN CTION  IT 3       I  ID TI      T COND IT TO T       I      T AND       ITC	.

3.      I      T  I T        A     B  A T      BI T       INC  I T	 N  1	2.
 I T	     A      A      O TIONA C I IN  O NT AND  O NT D ON C I IN O 	      COO      .

1	PARTIAL BUILDING 'K' ELECTRICAL ROOF PLAN
 	 CA      1       1     

 11 	 132

 121
 13 	 133

GENERAL NOTES  

1.      A     COND IT      N T ATION   A     B   A D  IT A	O  D
  A ANT TO 	 NT  OI T           N T ATION  IT IN T      	     
AND COO      .

CLOVIS, CA 93619
1560 N. MINNEWAWA AVE.
--------------------------
 11 	 11 

       N       1 	       N       
       N       2 	       N        C 2 
       N   	C 1 
       N        
       N  	

 12 

 123

 12 

 122

           C 2    2

       C 2 2,       	 

 N COO	 I  T 
       C 2      

 12 	 12 

 N COO	 I      T 
  	C 2       

1

2     C 2      

   	  C C C

1	 12 
   	C 2       ,     

 	2

3	3

T .	T .	   	C 2       , 2

 	3

 N 	 I      T 
       C 2      

 12 

Fresno, CA 93720
FAX (559) 431-1362
G R O U P
2	PARTIAL BUILDING 'K' ELECTRICAL FLOOR PLAN
 	 CA      1	1  

7084 N. Maple Ave., Suite 101
(559) 431-0101
E N G I N E E R I N G
TITLE:

		

Borrelli
Cons ltin 
2 32 N.  a
 resno, CA.
     one 	
 tt	
ca ai      or BAI 22111
					
c.

&
 lec
te 
 3
 23 . o
relli
	
Associates, In trical  n ineers
a Bo le ar 
 2 
3 13 
rrellien ineerin .co     
en ineerin .co 

PARTIAL BUILDING 'K'	

ELECTRICAL ROOF &

FLOOR PLAN

CO  I      T 2 22 B BO	I AND A OCIAT , INC. A      I      T 	D T       I	O BO	I AND A OCIAT , INC. AND IT      B IDIA     CO      ANI 
                  IT CO       ON  A     CO      I      T AND OT       A  ICAB          O      T  I      T IN T           AN . T         AN A      NOT TO B          OD C D, C AN     D, O CO I D IN AN  O       O  ANN             AT O         , NO A      T        TO B A  I N D TO A T I D  A T  IT O T  I T OBTAININ T            ITT N           I  ION AND CON NT O BO          I AND A OCIAT , INC. AND IT      B IDIA     CO      ANI . IN T             NT O AN  NA T O I     D              O T         AN B A T I D
 A T , T      T I D  A T      A      O D T       I	O BO	I AND A OCIAT , INC. AND IT      B IDIA     CO      ANI      A	     AND   A     B A T      CO T O 
BO	 I AND A  OCIAT , INC. AND IT      B IDIA     CO      ANI     	A  	A OCIAT D  IT D	NDIN AND  N O CIN T	  I      T .

SHEET: E3.02

PROJECT	21191

	cational Clo is     D B c anan i      c ool Col Bo e lace ent 22111 3 2.	, 12 3 2 22 3 31	      ,  2 32, A toCAD  D  i	      alit  rint . c3, A C  ll  lee D  3 .	 2 .	Inc es 

A
B
DSA

		        . BOA D
	COAT D  OOD  C      
 IN. 2       B D      NT
		
		AND  A	, T ICA 
		
					1

	

3	COND IT
2	 

COND IT	 
1
3

1

 	2
3	 

 

 

SHINGLE ROOF
	ROLL ON ROOF

D TAI NOT            
1.	T  ICA O   . T ICA  A	 OO IN NAI ,
 I       ON T	3     NN  2 1     a. AT A      O  
CO N	O T       OO  AC .  A  AC NAI  IT 
     BB     I     D  A TIC.
2.	      TA  OO  A     IN      AC . 3.	 A  IT      BB     I     D  A TIC.
 .	     I TIN  OO   IN	,  I  OO  AC 
B N AT   IN	.
 .	NAI  OO  AC AT      	 ID O  OO B N AT 	
     IN	.  A  IT  A TIC.
	
D TAI NOT     	 
1.        A  A TIC. 2.      OO  AC .
3.     	O      CA 	T,  T  OO  AC IN  OT A      A T O 
     BB     I     D  OO  A TIC.
 .     NOT 	D.
 .     A	   IB      TA     C NT	D ON 	I      T      O  OO 
 AC BA     IN  OT A	A T.
 .     COND IT.
 .     CA	 O C D INTO   AC TO  A I	  T NT  O  IB .
CA	     A     B IN TA      D 	       IT  OO 	B AN 
AND C I IN .

 N	      AN NO  AT     
CAN      N T AT B T	N TO 
D     TIT  I    A	C T TO  I     	O BOOT &  I     .
 I      IN  I D  O T AT   A     IN 
 IT  N 	A O ND  I     
 T BA     IN CONTIN O      B AD O A  O     D  A ANT.
 TANDIN   A      OO 

  IO TO  IDIN D     TIT DO N O	 I      AC A CONTINO      B AD
O A	O     D  A ANT A O ND  I     
AT T           I      T O T      BOOT  O T AT
	 N T  BOOT I IN  AC T  TO 
O T      BOOT  N A	T       A ANT.
	
STANDING SEAM ROOF
	
NOT     
1.	T  D     TIT COND IT   A     IN 	T B  A T N D TO T       AN     ON  AND NOT INTO T       OO   B T AT TO A O 
T   AN     TO  O      T	A      .
2.	AD	AT C A ANC 	T B       T B T	N T      COND IT AND T       AN     TO A  O      O T	A  O 	NT
 IT O T INT	NC .
3.	T  COND IT 	T B C NT	D IN T       AN     TO A O     AD	AT C  A ANC  O IN TA ATION O T      D     TIT 
 IT O T INT	NC  IT T       AN      IB .
 .	 O 	ION  IT  NO     & IC , A  O     O  NO           A D 	T B IN TA      D NO 	AT  T AN 3 IN      ONT O T     
COND IT      N T ATION  O      OT CTION.
 .	COND IT  A	T AN   IN DIA      T       A 	I      A C     B D      NDIN ON  AN      IDT & COND IT  OCATION. T I I 
TO B 	I I D IN  I D.

2
	TYPICAL CONDUIT ROOF PENETRATIONS

 

		NOT TO  CA 

                 	CAN	TO  NI T     T      IN 
 NI T     T       IN N T 
AND BO T . T ICA AT A 
 O      CO N      O  AC 
 BO	I	A , T  .

 A T N  NI T  T
C ANN     TO  AC  OOD
 T D  IT  A BO T  IT 
A  INI	O 2 1 2 INC 
     N T ATION. T ICA O 
  C 	         BO .
 N  NI T     T
     1	T	, T  .	       T D  A 

       T D, T .

COND IT, T .

1
	WALL MOUNTED J-BOX/WIREWAY DETAIL

 

		NOT TO  CA 

APPROVALS: APPLICATION #

3 
O       A 

   T     CT     A 
 OI T
1     ON C NT     	 1 2 1 2       AT	

1

 A T N  BO	I	A 	      IDENTIFICATION STAMP DIV. OF THE STATE ARCHITECT

APP:02-120017 INC: REVIEWED FOR

FLS	ACS
✔	✔
SS ✔            DIVISION OF THE STATE ARCHITECT D E P A R T M E N T O F G E N E R A L S E R V I C E S

DATE:	03/01/2023	

 NI T  T TO B IN TA      D 	
1	T  A I	A ON T     
COND IT   N, AND  IT IN
1 INC      O  	COND IT
 AT C AN  IN DI     CTION.

CONDITION 1  C I IN  O NT D

C I IN  OI T  A A       TO COND IT      N

   T     CT  A 
 OI T

T ICA COND IT

T ICA  NI T     T
 I  COND IT C A      

       T     CT     A 
	 A 

 1     2 1 2   AT	
COAT D  OOD  C           IN. 2       B D      NT AND
 A	, T ICA 

 NI T     T TO B IN TA      D 	1 	T
 A I	A ON T      COND IT      N, AND
 IT IN 1 INC	O 	COND IT  AT 
C AN      IN DI     CTION.

T  ICA COND IT

T ICA  NI T     T
 I      COND IT C A      

R
No. M34846 Exp. 6-30-24

A

DATE:	8-9-2022

	
3  IN T .

				

D CONDITION   COND IT  O NTIN ON        A 

T  ICA COND IT

T  ICA  NI T  T
 I      COND IT C A  

1

 NI T     T TO B IN TA  D 	1 	T
 A I           A ON T      COND IT      N, AND
 IT IN 1 INC      O 	COND IT  AT 
C AN      IN DI     CTION.

T ICA  NI T     T
 I  COND IT C A      

T ICA COND IT

1

 NI T  T TO B IN TA      D 	
1 	T  A I	A ON T  
COND IT      N, AND  IT IN 1  INC      O 	COND IT
 AT C AN      IN DI     CTION.

CONDITION 2  C I IN  O NT D
C I IN  OI T            NDIC     A TO COND IT      N

      C I IN  OI T	      C I IN 
 1     2 1 2   AT	
COAT D  OOD  C       
 IN. 2   B D      NT
AND  A	, T ICA 

3 
O	A 

CLOVIS, CA 93619
1560 N. MINNEWAWA AVE.
--------------------------
COLD BOX REPLACEMENT
BUCHANAN HIGH SCHOOL
COND IT
E

3  IN T  .

				

					

CONDITION   ABO      C I IN  O NT D 1	C I IN  OI T  A A	TO COND IT      N

       T  CT     A 
 A      T D

 NI T     T TO B IN TA      D 	1 	T
 A I	A ON T      COND IT      N, AND
 IT IN 1 INC      O 	COND IT  AT 
C AN      IN DI     CTION.

T ICA  NI T     T
 I      COND IT C A      

 NI T     T TO B IN TA  D 	1	T
 A I	A ON T      COND IT   N, AND
 IT IN 1 INC	O            COND IT  AT 
C AN      IN DI  CTION.

1

T ICA  NI T     T
 I  COND IT C A      

 3 1 B     B TIT 
 I     T    A IN 
T ICA COND IT

 A	 2 O.C.

      C I IN 
3  IN	 OI T T .

	

T ICA COND IT

F
CONDITION   ABO      C I IN  O NT D

C I IN  OI T            NDIC     A TO COND IT   N

C CONDITION 3   A      O NT D

DETAIL NOTES  

1.          O ID AND IN TA      NI T  T COND IT C A       . COO DINAT  NI T     T 	B       I     . 	TO  C     D	B O      O C A	 OD     N      B      AND  A I	COND IT  I      	C A      .

GENERAL NOTES

1.	      ANTIT O COND IT ON  NI T     T  O NT D  A  A     . 	TO COND IT  O TIN  OO  AN  O       ANTIT O COND IT.

2.	 O COND IT  O TIN  A A	TO T   OO  OI T  IT A       I      T 	AT      T AN 1 B . T., T            O T      A     B  IT IN 2 	T O AN      I TIN  T     CT     A B A , ON 	 O T ON  AC  ID O T      B A .

3.	COND IT  O TIN            NDIC  A TO T       OO  OI T  IT A   I  T       AT      T AN 2 B .  T.      A     B  IT IN 2 	T O AN      I TIN  T     CT     A 	A .

 .	 NI T  T C ANN       A     B  1	,  ON. COO DINAT  NI T     T 	B   I     .

REVISIONS
7084 N. Maple Ave., Suite 101
(559) 431-0101
Fresno, CA 93720
FAX (559) 431-1362
E N G I N E E R I N G
G R O U P
TITLE:

TYPICAL DETAILS	

 	TYPICAL CONDUIT SUPPORT DETAIL

NOT TO  CA 

CO  I      T 2 22 B BO	I AND A OCIAT , INC. A      I      T 	D T       I	O BO	I AND A OCIAT , INC. AND IT      B IDIA     CO      ANI 
                  IT CO       ON  A     CO      I      T AND OT       A  ICAB          O      T  I      T IN T           AN . T         AN A      NOT TO B          OD C D, C AN     D, O CO I D IN AN  O       O  ANN             AT O         , NO A      T        TO B A  I N D TO A T I D  A T  IT O T  I T OBTAININ T            ITT N           I  ION AND CON NT O BO          I AND A OCIAT , INC. AND IT      B IDIA     CO      ANI . IN T             NT O AN  NA T O I     D              O T         AN B A T I D
 A T , T      T I D  A T      A      O D T       I	O BO	I AND A OCIAT , INC. AND IT      B IDIA     CO      ANI      A	     AND   A     B A T      CO T O 
BO	 I AND A  OCIAT , INC. AND IT      B IDIA     CO      ANI     	A  	A OCIAT D  IT D	NDIN AND  N O CIN T	  I      T .

SHEET: E4.01

		

Borrelli
Cons ltin 
2 32 N.  a
 resno, CA.
     one 	
 tt	
ca ai      or BAI 22111
					
c.

&
 lec
te 
 3
 23 . o
relli
	
Associates, In trical  n ineers
a Bo le ar 
 2 
3 13 
rrellien ineerin .co     
en ineerin .co 

PROJECT	21191

       cational Clo is  D B c anan i       c ool Col Bo  e lace ent 22111      1.       , 2 1 2 23  13       A ,  A2 32, A toCAD  D      i    alit  rint . c3, A C  ll  lee D  3 .       2 .      Inc es 

DSA
IDENTIFICATION STAMP DIV. OF THE STATE ARCHITECT

APP:02-120017 INC: REVIEWED FOR

FLS	ACS
✔	✔
SS ✔            DIVISION OF THE STATE ARCHITECT D E P A R T M E N T O F G E N E R A L S E R V I C E S

DATE:	03/01/2023	

R
No. M34846 Exp. 6-30-24

A

STRUCTURAL

DETAILS

S1.0